## Sheet1
Generator Replacement Plan | [6 empty] | Need this Data for Generator Sizing
Units | Prioritized Locations | Maximo Location Number | GRID | FM > 12" | Peak Flow (GPM) | Class of Station (1 - 4 ) | System Voltage (Volts) | Existing Service Size (AMPs) | # of Motors | HP of Motors | Motor Type (NEMA, IEC, …) | Starting Method * VFD * Soft Start * Across the Line | Starting Code (E, F, G, ...) | Other Loads requiring Generator power (AMPs) | MAXIMUM Voltage Dip (%) | Calculated Gen Size (kW) | ATS Size | Fuel Tank Size | Coment
1 | 1001 Broward Rd | LS-000484 | North |  |  | 3 | 480 | 200 | 2 | 60 |  | Across the Line |  | 30 | 20% |  |  |  | ATS with Bypass required
2 | 7732 Merrill Rd | LS-001452 | East | 6 |  | 2 | 240 | 125 | 2 | 15 |  | Across the Line |  | 30 | 20% |  |  |  | ATS Installed FY 18
3 | 4770 Cisco Rd | WTP-4770 | Water |  |  | NA | 480 | 1200 | 4 | SP1 - 40 SP2 - 75 SP3 - 150 Well 2 30 | TDS | SP1 - VFD SP2 - VFD SP3 - SS Well 2- SS | SP1 - F SP2 - G SP3 - G Well 2- G | 30 | 20% | 300 KW |  |  | Replacing exsiting unit same size.
4 | 10797 Ft Caroline Rd | LS-000915 | East | 8 |  | 3 | 480 | 600 | 2 | 45 |  | VFD |  | 30 | 20%
5 | 7615 Pritchard Rd | LS-002416 | West |  |  | 3 | 480 | 200 | 3 | 25 |  | Across the Line |  | 30 | 20% |  |  |  | ATS with Bypass required
6 | 6462 Harvin Rd | LS-001030 | East | 4 |  | 2 | 240 | 200 | 2 | 20 |  | Across the Line |  | 30 | 20%
7 | 1870 41St St W | LS-000009 | North |  |  | 3 | 480 | 200 | 2 | 25 |  | Across the Line |  | 30 | 20% |  |  |  | ATS with Bypass required
8 | 10000 Deer Creek Club Rd E. | LS-000699 | South |  | 1000 | 3 | 480 | 600 | 3 | 60 |  | Soft Start |  | 30 | 20% |  |  |  | the mcc has a 300 amp main breaker, the station disconnect is 600 amps. The pumps are 56 hp. ATS with Bypass required
9 | 8431 Springtree Rd | LS-002133 | West | 16 |  | 3 | 480 | 400 | 3 | 57 |  | Across the Line |  | 30 | 20% |  |  |  | ATS with Bypass required
10 | 2434 Pearl St | 2434-PEA | Admin |  |  | NA |  |  | NA | NA | NA | NA | NA | NA | 20% | 175 |  |  | Replacing exsiting unit same size.
11 | 6801 Rhone Dr | LS-001863 | North |  |  | 3 | 240-3P | 400 | 2 | 25 |  | Soft Start |  | 30 | 20% |  |  |  | ATS with Bypass required
12 | 2520 Orange Picker Rd | LS-001687 | South |  | 1200 | 3 | 480 | 400 | 3 | 60 |  | VFD |  | 30 | 20% |  |  |  | ATS with Bypass required
13 | 10656 Kennedy Ln | LS-001178 | South |  | 2400 | 4 | 480 | 400 | 3 | 60 |  | VFD |  | 30 | 20% |  |  |  | ASCO 300 ats Replaced FY 15 Save and Replace with ATS with Bypass required. The pumps are 57HP.
14 | 5791 Atlee Ave | LS-000214 | West |  |  | 3 | 240 | 400 | 2 | 56 |  | VFD |  | 30 | 20% |  |  |  | ATS with Bypass required
15 | 2801 Suni Pines Blvd | LS-000300 | East |  |  | 2 | 240 | 250 | 2 | 20 |  | Across the Line |  | 30 | 20%
16 | 1767 Sandlewood Blvd | LS-002009 | East |  |  | 2 | 240 | 250 | 2 | 25 |  | Across the Line |  | 30 | 20%
17 | 4110 Atlantic Blvd | LS-000173 | East |  |  | 3 | 240 | 250 | 2 | 20 |  | Across the Line |  | 30 | 20%
18 | 1705 Hodges Blvd | LS-001089 | East |  |  | 3 | 240 | 200 | 2 | 20 |  | Across the Line |  | 30 | 20%
19 | 12928 Palmetto Glade Dr | LS-001627 | East |  |  | 2 | 240 | 250 | 2 | 15 |  | Across the Line |  | 30 | 20%
20 | 13383 Tropic Egret Dr | LS-002308 | East |  |  | 4 | 480 | 225 | 3 | 40 |  | Soft Start |  | 30 | 20%
21 | 11789 Saints Rd | 11789-WTP | Water | NA | 12900 | N/A | 480 | N/A | N/A | N/A | N/A | Soft Start |  | 30 | 20% | 500 |  |  | Replacing exsiting unit same size.
22 | 7615 Southside Blvd | 10357-DEER | Water | NA | 26802 | N/A | 480 | N/A | N/A | N/A | N/A | VFD Soft Start |  | 30 | 20% | 500 |  |  | Replacing exsiting unit same size.
23 | 8032 Pointmeadows Dr | LS-001787 | South |  |  |  | 480 | 300 | 2 | 56 |  | VFD |  | 30 | 20%
24 | 2935 Orange Picker Rd | 2935-WTP | Water | NA | 11900 | N/A | 480 | 1200 | 6 | SP1 - 200 SP2 - 200 SP3 - 125 SP4 - 125 SP5 - 60 SP6 - 60 | NEMA | Soft Start | SP1 - F SP2 - F SP3 - G SP4 - F SP5 - F SP6 - G | 30 | 20% | 500 KW |  |  | Replacing exsiting unit same size.
25 | 4437 Barnes Rd | LS-000230 | East |  |  | 3 | 240 | 250 | 3 | 15 |  | Across the Line |  | 30 | 20%
26 | 5420 118th St | LS-000258 | West |  |  | N/A | 480 | N/A | N/A | N/A | N/A |  |  | 30 | 20% | 1500 KW |  |  | No ATS - MCC switch gear - Replacing exsiting unit same size.
27 | 220 Davis Pond Rd | 220-WWTP | St Johns |  |  |  | 480 | 1600 | 25 | 2HP to 150HP |  | 1 VFD 1 SS |  | 150 | 20% | 750 KW |  |  | Maintenance coordinator indicated 800 KW will carry the plant.
28 | 2455 Hawkcrest Dr | 2369-WTP | Water | NA | 3060 | N/A | 480 | 800 | 3 | SP1 - 30 SP2 - 50 SP3 - 75 | NEMA | VFD | SP1 - G SP2 - G SP3 - F | 30 | 20% | 400 KW |  |  | Replacing exsiting unit same size.
29 | 4618 Clyde Dr | LS-000593 | North | 12 |  | 2 | 480 | 400 | 2 | 56 |  | VFD |  | 30 | 20%