## SOS
JEA | [6 empty] | Request for Proposal
418692.67.9100 |  | Power Island Equipment |  |  |  |  | 2024-09-09
Technical input to 00300.2 Schedule of Submittals and Applicable Liquidated Damages
Item No. | Reference Document | Submittal Item | Submittal Dates |  |  |  | LD's Apply?
|  |  | Calendar Days |  | Event | Due Date
Schedule of Submittals
| 5135 | Steel Stack Designed by Supplier |  |  | .
04xx | 5135 | Structural Steel Material Certification |  |  | Upon request
04xx | 5135 | High Strength Bolts Material Certification |  |  | Upon request
04xx | 5135 | Direct Tension Indicators Material Certification |  |  | Upon request
06xx | 5135 | Grating Copies of Certified Test and Inspection Reports | 14 | After | Test/Inspection
05xx | 5135 | Arrangement drawings | 30 | After | Effective Date
06xx | 5135 | Foundation design requirements | 30 | After | Effective Date
06xx | 5135 | Design calculations | 30 | After | Effective Date
05xx | 5135 | Fabrication and erection detail drawings | 30 | After | Effective Date
06xx | 5135 | Stack, liner, insulation, and lagging materials specifications | 30 | After | Effective Date
06xx | 5135 | Shop and/or field coatings data | 30 | After | Effective Date
| 11508 | Ammonia System |  |  | .
05xx | 11508 | Detailed arrangement drawings indicating pipe connection points | 30 | After | Effective Date |  | No
05xx | 11508 | Installation Drawings and Erection Procedures | 60 | Before | Shipment |  | No
05xx | 11508 | Load and foundation requirements | 30 | After | Effective Date |  | No
06xx | 11508 | Fan performance curve - final | 30 | Before | Shipment |  | No
06xx | 11508 | Flowmeter certification report | 30 | Before | Shipment |  | No
05xx | 11508 | Hazardous Area Layout Drawings for all areas where explosive gasses or dusts are introduced by the supplied equipment. | 60 | After | Effective Date |  | Yes
| 13125 | Pre-Manufactured Metal Equipment Building |  |  | .
06xx | 13125 | Bill of Material, Including Quantity, Description, and Part Number |  |  | Effective Date |  | No
05xx | 13125 | Plan view outline - General arrangement, center of gravity weight, floor opening size and locations, mounting details, and cable entry area and door swing requirements | 30 | After | Effective Date |  | No
05xx | 13125 | Elevation outline - General arrangement in elevation, recommended pier and tie-down locations, and wall opening sizes and locations | 30 | After | Effective Date |  | No
05xx | 13125 | Legend/design criteria outline - Design criteria and drawing legend | 30 | After | Effective Date |  | No
05xx | 13125 | Electrical interconnection diagram | 30 | After | Effective Date |  | No
06xx | 13125 | Bolt torque verification records for all mechanical connections of electrical bus bar connected by pre-manufactured metal equipment building fabricator. | 30 | Before | Shipment |  | No
06xx | 13125 | Certified design calculations | 30 | After | Effective Date |  | No
06xx | 13125 | Bill of Material, Including Quantity, Description, and Part Number |  |  |  |  | No
05xx | 13125 | Submit drawings indicating the layout of building |  |  |  |  | No
| 15272 | Bypass Valves |  |  | .
440 | 15272 | Copies of Certified Test and Inspection Reports | 0 | With | Instruction Manual |  | No
06xx | 15272 | Certified Material Test Report (CMTR) indicating aluminum content not exceeding 0.08 percent, or documentation demonstrating compliance with ASTM A703 S23 requirements, for each casting furnished as a pressure-retaining component and with a design temperature greater than 210°F (99°C). |  | Upon | Receipt of Casting at Supplier's Shop |  | No
05xx | 15272 | Installation Drawings and Erection Procedures | 60 | Before | Shipment |  | No
04xx | 15272 | Requirements for disassembly of valves for preheat, welding, and PWHT, including critical temperature thresholds for any points on the valve body/actuator |  | Upon | Shipment of Equipment |  | No
442 | 15272 | Documentation of body casting repairs, including postweld heat treatment records and re-examination records | 0 | With | Instruction Manual |  | No
443 | 15272 | Radiograph reports in accordance with ANSI B16.34 | 0 | With | Instruction Manual |  | No
444 | 15272 | Shell pressure test and seat leakage test reports (for tests required by ASME B16.34 and ANSI/FCI 70-2) | 0 | With | Instruction Manual |  | No
446 | 15272 | Quality Manual, controlled copy | 30 | After | Effective Date |  | No
448 | 15272 | Subsupplier listing | 5 | Before | Issue of Subsupplier Purchase Order |  | No
449 | 15272 | Inspection and test plan | 30 | Before | Start of Fabrication |  | No
450 | 15272 | Notification of inspection/test (for B&V hold/witness points) | 14 | Before | Test/Inspection |  | No
451 | 15272 | Welding Procedure Specifications (WPS) with applicable Procedure Qualification Records (PQR) | 30 | Before | Start of Fabrication |  | No
452 | 15272 | Procedures for storing, issuing, and reconditioning of electrodes, wires, and fluxes | 30 | Before | Start of Fabrication |  | No
453 | 15272 | Repair procedures | 5 | After | Discovery of Repair Need |  | No
454 | 15272 | Post-weld heat treatment procedures | 30 | Before | Start of Fabrication |  | No
455 | 15272 | Visual inspectors' qualifications and certificates | 30 | Before | Start of Fabrication |  | No
456 | 15272 | Root side purging procedures | 30 | Before | Start of Fabrication |  | No
457 | 15272 | Nonconformance reports | 5 | After | Discovery of Nonconf. |  | No
458 | 15272 | Nondestructive examination procedures | 30 | Before | Start of Fabrication |  | No
460 | 15272 | Paint surface preparation, primecoat, finish coat, and touch up specification data sheets. | 45 | After | Effective Date |  | No
534 | 15272 | Wiring and elementary diagrams showing all external control/instrumentation connections. | 60 | After | Effective Date |  | Yes
535 | 15272 | Dimensional drawings including overall dimensions, detailing all power, control and instrumentation junction box sizes and locations and maximum power, control and instrumentation cable termination requirements. Also provide ground lug size and location, if specified or furnished. | 60 | After | Effective Date |  | Yes
562 | 15272 | Data Sheets with Design and Operating Conditions | 14 | After | Effective Date |  | Yes
563 | 15272 | Valve/Actuator Assembly Outline Drawings, Including Dimensions (End-to-End, Removal), Weight, Center of Gravity, Direction of Flow, Pipe Connection Details, and List of Accessories | 14 | After | Effective Date |  | Yes
566 | 15272 | Flow Data; Cv, Cg, or Cs Versus Valve Opening for All Valve design cases. | 14 | After | Effective Date |  | No
570 | 15272 | Steam Blow and Hydro Kits Including Any Piping Connection Details, Overall Dimensions, Weights, and Bill of Materials | 60 | After | Effective Date |  | No
571 | 15272 | Limit switches, solenoid valves, positioners, position transmitter data including make, model, electrical ratings, and physical arrangements. (Vendor only needs to submit once if components don't change from one valve to the next.) | 60 | After | Effective Date |  | Yes
574 | 15272 | Final As-Built Drawings and Documentation (Only if different from previously submitted drawings) | 30 | After | Final Acceptance |  | No
721 | 15272 | Valve pneumatic tubing diagrams with bill of material | 60 | After | Effective Date |  | No
724 | 15272 | Sectional drawing showing materials and internal construction | 60 | After | Effective Date |  | No
900 | 15272 | ASA Valve Flow Equation Coefficients | 60 | After | Effective Date |  | No
901 | 15272 | Compressed Air Volume Tank Outline Drawings with dimensions, weights, and pipe connections | 30 | After | Effective Date |  | No
902 | 15272 | Compressed Air Volume Tank ASME Code Certifications |  | With | Instruction Manual |  | No
| 15511 | Heat Recovery Steam Generator |  |  | .
05xx | 15511 | HRSG shipping configuration, number of modules, module weight, and dimensions | 15 | After | Effective Date |  | No
05xx | 15511 | Notice of HRSG physical flow model test - if required | 30 | Before | Test |  | No
05xx | 15511 | Computer 2D flow model simulation or physical flow model test report as applicable | 30 | After | Test or Inspection |  | No
05xx | 15511 | ASME Code Data Package | 30 | After | Last shipment of pressure part equipment. |  | No
05xx | 15511 | ASME code certifications | 60 | After | Effective Date |  | No
06xx | 15511 | Arrangement drawings and terminal point locations for plant layout and physical arrangement and dimensions of equipment furnished | 60 | After | Effective Date |  | Yes
06xx | 15511 | Instrument and valve location drawings indicating the location of all instruments and valves which require air, electrical, or control interface with Purchaser | 210 | After | Effective Date |  | Yes
05xx | 15511 | Stair tower arrangement drawings | 75 | After | Effective Date |  | No
05xx | 15511 | Certification document by Accredited Elevator Certification Organization for the manlift. | 30 | Before | Shipment |  | No
05xx | 15511 | Manlift arrangement drawings | 60 | Before | Shipment |  | No
05xx | 15511 | Manlift erection/installation drawings | 60 | Before | Shipment |  | No
06xx | 15511 | Duct outline drawings including movements and clearances for insulation, lagging, stiffeners, expansion joints, and acoustic shrouds (if furnished) | 75 | After | Effective Date |  | No
05xx | 15511 | Drum End Enclosures: General arrangement drawings; HVAC calculations; lighting design. | 180 | After | Effective Date |  | No
05xx | 15511 | Loads for design of Purchaser's structures | 60 | After | Effective Date |  | Yes
06xx | 15511 | Stack: PE certified Calculations per ASME STS-1; Base ring diameter; Anchor Bolt circle; Recommended grout thickness; Anchor bolt size, layout, and materials (i.e. A36, A307, etc.) | 30 | After | Effective Date |  | No
06xx | 15511 | Foundation Design Information: Loads listed seperately (i.e. Dead, Live, Seismic, wind, thermal, etc.) for each support clearly indicating load direction at each support for each load case; equipment/steel thermal growth, plan dimensions, thicknesses, and elevations of sole plates, sub-sole plates; shear posts, shear lugs; Delineation of scope of supply for all sole plates, sub-sole plates, shear posts, shear lugs, etc.; Locations, plan size, thickness of all auxiliary supports at grade for ladders, stairs, and platforms. Anchor bolt sizes, locations, and materials (i.e. A36, A307, etc.) | 30 | After | Effective Date |  | No
07xx | 15511 | Design pressure, temperature, flow rate, and set point of safety valves. | 45 | After | Effective Date |  | No
05xx | 15511 | Valve list including valve size, design temperature and pressure class, etc. | 90 | After | Effective Date |  | No
05xx | 15511 | Pipeline list including design temperature, pressure, material, schedule, and size for all pipe furnished. | 75 | After | Effective Date |  | No
05xx | 15511 | Preliminary high pressure main steam, hot reheat, and cold reheat steam line terminal point information including design conditions (press, temp, flow), outside diameter, wall thickness, materials, 3D locations, thermal movements, and allowable forces and moments | 45 | After | Effective Date |  | Yes
05xx | 15511 | Terminal point information, including design conditions (press, temp, flow), outside diameter, wall thickness, materials, 3D locations, thermal movements, and allowable forces and moments, for the remaining systems | 60 | After | Effective Date |  | Yes
05xx | 15511 | Large bore piping isometric drawings - Including valve, pipe, and equipment weights and stress | 60 | After | Effective Date |  | Yes
05xx | 15511 | Small bore piping isometric drawings (including suggested routing for blowdown and drain piping and header) | 210 | After | Effective Date |  | No
05xx | 15511 | Safety relief valve, continuous vent, and trim piping drawings for deaerator | 140 | After | Effective Date |  | No
05xx | 15511 | Hanger details | 90 | After | Effective Date |  | No
06xx | 15511 | Piping and instrument diagrams indicating all piping, valves, and instrumentation being supplied by the Contractor and clearly identifying all interfaces with the Purchaser | 45 | After | Effective Date |  | Yes
06xx | 15511 | Dimesional drawings including overall dimesions, detailing all power, control and instrumentation junction box sizes and locations and maximum power, control and instrumentation cable termination requirements. Also provide ground lug size and location, if specified or furnished. | 60 | After | Effective Date |  | Yes
05xx | 15511 | Detailed wiring diagrams showing all external connections | 60 | After | Effective Date |  | No
05xx | 15511 | Functional description of the operation of equipment (Final for HRSG, preliminary for burner and SCR) including HP and LP steam turbine bypass system design and operational requirements | 90 | After | Receipt of Final Plant Operating Philosophy Document |  | No
07xx | 15511 | Functional description of the operation of SCR and burner | 180 | After | Effective Date |  | No
06xx | 15511 | HRSG I/O list with termination information including SCR and BMS | 120 | After | Effective Date |  | No
06xx | 15511 | Instrument data sheets (ISA type or equal) and installation details for control system including estimated impulse tubing requirements | 180 | After | Effective Date |  | No
06xx | 15511 | Detailed list of instrumentation and control equipment listing manufacturer, model number, range, setpoint, signal level, etc | 210 | After | Effective Date |  | Yes
06xx | 15511 | Complete unit performance data including all flue gas, steam, and water flows, pressures, pressure drops, and temperatures and duct burner fuel gas flows for all full and part load heat balance cases | 60 | After | Effective Date |  | No
06xx | 15511 | Steam temperature curves for high-pressure superheater outlet temperature under clean, normal, and dirty surface conditions (oil fired only) | 60 | After | Effective Date |  | No
06xx | 15511 | Temperature profiles of the HRSG gas side | 60 | After | Effective Date |  | No
06xx | 15511 | Performance curves for auxiliary equipment including pump performance curves | 210 | After | Effective Date |  | No
06xx | 15511 | Maximum allowable working pressure of the HRSG as defined by the ASME Boiler and Pressure Vessel Code | 75 | After | Effective Date |  | Yes
04xx | 15511 | HRSG startup characteristics for cold and hot starts, time in hours shall be the abscissa, the ordinates shall be steam pressure, temperature, and flow along with exhaust temperature for the HP, IP, and LP systems | 90 | After | Receipt of CTG Start-up curves and Purchaser's start-up philosophy documents |  | No
04xx | 15511 | Duct burner emission curves indicating NOx, CO, and VOC/UHC predicted emissions on a mass basis for the entire operating range of the duct burner | 210 | After | Effective Date |  | No
04xx | 15511 | Water volumes of the various sections of the HRSG | 75 | After | Effective Date |  | No
04xx | 15511 | Station and Instrument air requirements (Total Not-to-Exceed) | 45 | After | Effective Date |  | Yes
04xx | 15511 | HRSG Purge volume | 60 | After | Effective Date |  | No
04xx | 15511 | PC based computer thermal model of HSRG | 210 | After | Effective Date |  | No
04xx | 15511 | Guaranteed and expected steam quality leaving each drum separator over the entire operating range | 60 | After | Effective Date |  | Yes
04xx | 15511 | HRSG fabrication and erection drawings | 120 | After | Effective Date |  | No
04xx | 15511 | Recommended detailed erection sequence and procedure | 120 | Before | Shipment of First Delivery of Steel Structure |  | No
06xx | 15511 | Insulation requirements and details including detailed insulation specifications, drawings, and instructions for field installation | 30 | Before | Shipment of Equipment |  | No
06xx | 15511 | Package for preoperational cleaning of the HRSG. The submittal shall include the manufacturer’s chemical cleaning procedures or guidelines, calculations of the operating and hydro boiler volumes by section, HRSG P&ID’s, HRSG general arrangement and elevations, bundle arrangement drawings, and isometric drawings of the main steam and reheat attemperator piping. The bundle arrangement drawings shall indicate the number and size of tubes in each boiler section, and the flow configurations through them (i.e. ventable and drainable headers, or U-tubes). | 180 | After | Effective Date |  | No
05xx | 15511 | Hazardous Area Layout Drawings for all areas where explosive gasses or dusts are introduced by the supplied equipment. | 60 | After | Effective Date |  | Yes
| 15561 | Steam Turbine |  |  | .
06xx | 15561 | Lube and Control Oil specifications | 30 | After | Effective Date |  | No
06xx | 15561 | Power Island heat balances for load conditions specified | 30 | After | Effective Date |  | No
06xx | 15561 | Leakage flow and leakage enthalpy versus throttle flow curves | 30 | After | Effective Date |  | No
06xx | 15561 | Turbine exhaust loss curve | 30 | After | Effective Date |  | No
06xx | 15561 | Turbine exhaust pressure correction | 30 | After | Effective Date |  | No
06xx | 15561 | First-stage pressure versus flow to the following stage curve | 30 | After | Effective Date |  | No
06xx | 15561 | Reheat bowl pressure versus flow to the following stage curve | 30 | After | Effective Date |  | No
| 15561 | Correction curves for kilowatts for the following
06xx | 15561 | Throttle pressure rated +5 percent, -50 percent | 30 | After | Effective Date |  | No
06xx | 15561 | Throttle temperature rated +18° F to -50° F (+10°K to -28°K) | 30 | After | Effective Date |  | No
06xx | 15561 | Reheat temperature rated +18° F to -50° F (+10° K to -28°K) | 30 | After | Effective Date |  | No
06xx | 15561 | Reheater pressure drop 5 percent to 15 percent of HP turbine exhaust pressure | 30 | After | Effective Date |  | No
06xx | 15561 | Exhaust pressure from 1 inch Hga to the turbine maximum allowable continuous operating exhaust pressure | 30 | After | Effective Date |  | No
06xx | 15561 | All other correction curves for ASME PTC 46 Acceptance Test | 30 | After | Effective Date |  | No
06xx | 15561 | All curves in the Supplier's standard thermal kits | 30 | After | Effective Date |  | No
06xx | 15561 | Final list of motors including voltage, full load current, locked-rotor current, phase, horsepower, enclosure type for each motor, and space heater watts and volts | 90 | After | Effective Date |  | No
06xx | 15561 | Electrical load list including MOVs | 60 | After | Effective Date |  | No
06xx | 15561 | Final list of closed cycle cooling water requirements including flow and pressure drop | 45 | After | Effective Date |  | No
06xx | 15561 | Final list of all instrument/service air users and consumption | 90 | After | Effective Date |  | No
05xx | 15562 | Piping and Instrument Diagrams | 60 | After | Effective Date |  | No
05xx | 15561 | Drawings and procedure for lube oil flush showing all temporary pipe and equipment required |  | After | Effective Date |  | No
05xx | 15561 | Drawings indicating the location of all turbine generator junction boxes and electrical accessories requiring embedded conduit in the turbine generator pedestal, including recommended quantities and sizes of conduits into accessory | 90 | After | Effective Date |  | No
05xx | 15561 | Detailed schematic and wiring drawings of all electrical control wiring | 120 | After | Effective Date |  | No
05xx | 15561 | Drawings indicating the size and location of all turbine generator ground pads | 90 | After | Effective Date |  | No
05xx | 15561 | All drawings required to indicate miscellaneous piping and wiring connections and any other piping and wiring connections not indicated on previous drawings | 120 | After | Effective Date |  | No
05xx | 15561 | Arrangement drawings of all piping and accessories furnished, as required for the Purchaser's check of the layout of these items | 150 | After | Effective Date |  | No
05xx | 15561 | Drawings as required to indicate the details of construction and internal wiring of all equipment and equipment components furnished. Detail drawings of standard gauges, instruments, valves, and similar miscellaneous items | 60 | Before | Shipment of Equipment |  | No
06xx | 15561 | Lateral and torsional analysis report and critical speeds of turbine generator rotor | 60 | After | Effective Date |  | No
06xx | 15561 | Complete listing of all accessory equipment with instrument ranges and recommended contact set points | 150 | After | Effective Date |  | No
06xx | 15561 | Listing of accessory equipment to be shipped loose to jobsite | 30 | Before | Shipment of Equipment |  | No
05xx | 15561 | Drawings of all separately mounted equipment indicating information required for setting, piping, and wiring the items. This includes outline drawings of the supervisory instruments and accessory electrical equipment. | 120 | After | Effective Date |  | No
02xx | 15561 | Supplier to participate in design conference | 15 | After | Effective Date |  | No
06xx | 15561 | Equipment startup schedule duration requirements | 90 | After | Effective Date |  | No
06xx | 15561 | Specification data pages updated and resubmitted | 60 | After | Effective Date |  | No
| 15561 | Preservative coating data | 60 | After | Effective Date |  | No
06xx | 15561 | Detailed drawing submittal schedule list and submittal schedule | 30 | After | Effective Date |  | No
06xx | 15561 | Detailed data to describe the capability of the unit to operate at speeds above and below rated speed, including minimum and maximum allowable speed versus cumulative time duration of off normal speed operation | 60 | After | Effective Date |  | No
06xx | 15561 | All control devices and/or process set points, ranges, and flow quantities | 60 | After | Effective Date |  | No
06xx | 15561 | Complete I/O list for signals to/from Subsupplier's systems from/to Supplier's DCS | 120 | After | Effective Date |  | No
06xx | 15561 | I/O counts | 120 | After | Effective Date |  | No
05xx | 15561 | Detailed logic diagrams, operations procedures, and operator interface screens to implement control of Supplier's equipment via Purchaser's DCS | 120 | After | Effective Date |  | No
05xx | 15561 | Turbine generator general arrangement drawings. These drawings shall indicate all major equipment locations, access doors, maintenance or equipment removal space, and provide sufficient detail to allow for plan layout. | 30 | After | Effective Date |  | No
05xx | 15561 | All main steam, reheat steam, and large bore piping connection drawings including type, end prep details, allowable movements, and loads | 60 | After | Effective Date |  | No
05xx | 15561 | Details of temporary steam blow connections | 60 | After | Effective Date |  | No
05xx | 15561 | Condenser interface details including loading flange connections and loading conditions | 60 | After | Effective Date |  | No
05xx | 15561 | Drawings to assist Supplier in bus duct design/layout interface with generator ("bus duct" includes isophase bus duct and bus duct from generator neutral enclosure to the generator NGR enclosure) | 60 | After | Effective Date |  | No
06xx | 15561 | Flow charts detailing on-line monitoring programs for startup and on-line monitoring of critical parameters | 120 | After | Effective Date |  | No
05xx | 15561 | Preliminary erection drawings and detailed assembly instructions | 120 | After | Effective Date |  | No
05xx | 15561 | Final erection drawings and detailed assembly instructions | 360 | After | Effective Date |  | No
05xx | 15561 | Hazardous Area Layout Drawings for all areas where explosive gasses or dusts are introduced by the supplied equipment. | 60 | After | Effective Date |  | Yes
06xx | 15561 | Detailed drawing submittal list and submittal schedule | 60 | After | Effective Date |  | No
| 15562 | Combustion Turbine |  |  | .
06xx | 15562 | Lube and Control Oil specifications | 30 | After | Effective Date |  | No
06xx | 15562 | Certified design data and performance curves | 40 | After | Effective Date |  | No
05xx | 15562 | Arrangement Drawings required for plant layout indicating physical arrangement and dimensions of equipment furnished | 30 | After | Effective Date |  | No
05xx | 15562 | Arrangement Drawings for all auxiliary equipment indicating physical arrangement and dimensions of equipment furnished | 45 | After | Effective Date |  | No
05xx | 15562 | Foundation interface Drawings for all furnished equipment indicating loads, dimensions, anchor bolt locations, embedded conduit, and other necessary details | 45 | After | Effective Date |  | No
05xx | 15562 | Base combustion turbine generator unit arrangement and outline drawing | 30 | After | Effective Date |  | No
05xx | 15562 | CTG auxiliary enclosures and equipment arrangement and outline drawing | 45 | After | Effective Date |  | No
05xx | 15562 | Duct outline Drawings including movements and clearances for insulation, lagging, stiffeners, and expansion joints | 60 | After | Effective Date |  | No
05xx | 15562 | Detail Drawings indicating all Purchaser's piping and wiring connections including locations, sizes, types, materials, cable type, etc. | 60 | After | Effective Date |  | No
05xx | 15562 | Piping and Instrument Diagrams | 60 | After | Effective Date |  | No
05xx | 15562 | Equipment List for all major equipment being furnished | 60 | After | Effective Date |  | No
05xx | 15562 | Control panel and operator Work station outline and layout Drawings | 90 | After | Effective Date |  | No
05xx | 15562 | Drawings and data on accessory equipment including valves, fittings, and other components | 90 | After | Effective Date |  | No
05xx | 15562 | Electrical one-line diagrams indicating electrical scope | 60 | After | Effective Date |  | No
05xx | 15562 | Electrical elementaries, schematic, wiring, block and tubing diagrams, cable block diagrams, raceway layout, and cable entry into equipment | 120 | After | Effective Date |  | No
05xx | 15562 | Control system functional loop and logic diagrams | 90 | After | Effective Date |  | No
05xx | 15562 | HMI graphics display pages with descriptions of operator control actions linked to the graphics | 120 | After | Effective Date |  | No
05xx | 15562 | Control system and instrumentation input/output tabulations with descriptions and interface functions | 90 | After | Effective Date |  | No
05xx | 15562 | Hazardous Area Layout Drawings for all areas where explosive gasses or dusts are introduced by the supplied equipment. | 60 | After | Effective Date |  | Yes
06xx | 15562 | Instrument data sheets (ISA type or equal) and installation details for all control system input and output devices such as transmitters and control drives | 120 | After | Effective Date |  | No
06xx | 15562 | Recommended detailed erection sequence and procedure | 120 | Before | Shipment |  | No
06xx | 15562 | Electronic copy of the code data package for pressurized equipment, including pipe spools. Code data package to include the ASME data report forms, weld tracker, weld maps, Material Test Reports (MTRs), filler metal MTRs, heat number, NDE records, pre-heat weld heat treat charts, post weld heat treat charts, and calibration records for the chart recorder. |  | With | Shipment of Equipment |  | Yes
06xx | 15562 | Physical copies of the code data package for pressurized equipment, including pipe spools. Code data package to include the ASME data report forms, weld tracker, weld maps, Material Test Reports (MTRs), filler metal MTRs, heat number, NDE records, pre-heat weld heat treat charts, post weld heat treat charts, and calibration records for the chart recorder. |  | With | Shipment of Equipment |  | No
07xx | 15562 | Two draft copies of Commissioning Manual | 90 | Before | Start of commissioning |  | No
07xx | 15562 | Four final copies of Commissioning Manual | 30 | Before | Start of commissioning |  | No
05xx | 15562 | As-built Drawings | 60 | Before | Completion of commissioning |  | No
| 16031 | Cylindrical Rotor Generators |  |  | .
02xx | 16031 | Supplier to participate in design conference | 15 | After | Effective Date |  | No
06xx | 16031 | Generator hydrogen pressure correction curves for ASME PTC 6.1 acceptance test |  | Upon | Submittal of Proposal |  | No
06xx | 16031 | Generator power factor correction curves for ASME PTC 6.1 acceptance test |  | Upon | Submittal of Proposal |  | No
06xx | 16031 | Critical speeds of generator | 30 | After | Effective Date |  | No
06xx | 16031 | Generator loss curve and excitation power requirement curve including total electrical losses for generation capability at minimum hydrogen pressure and at 1 bar (14.5 psi) including up to the maximum hydrogen pressure for rated and unity power factors. Curve shall include the total mechanical or fixed losses. | 30 | After | Effective Date |  | No
06xx | 16031 | Cooling water requirements for the air/hydrogen coolers indicated as a curve for varying load conditions, hydrogen pressures, and cooling water temperatures | 30 | After | Effective Date |  | No
06xx | 16031 | Detailed data describing capability of the unit to operate above and below rated speed, including minimum and maximum allowable speed versus cumulative time duration of off-normal speed operation | 30 | After | Effective Date |  | No
06xx | 16031 | Reactive power capability versus real power capability curve at minimum and maximum hydrogen pressure(s) | 30 | After | Effective Date |  | No
06xx | 16031 | Generator "Vee" curves | 30 | After | Effective Date |  | No
06xx | 16031 | Zero and rated power factor current saturation curves | 30 | After | Effective Date |  | No
06xx | 16031 | No load saturation curves | 30 | After | Effective Date |  | No
06xx | 16031 | Generator allowable negative sequence versus time curve | 30 | After | Effective Date |  | No
06xx | 16031 | Generator current decrement curves for 3-phase, line-to-line, and line-to-neutral short-circuit conditions at the generator terminals | 30 | After | Effective Date |  | No
06xx | 16031 | Generator current decrement curves for 3-phase, line-to-line, and line-to-neutral short-circuit conditions at terminals of transformers connected to generator terminals. Electrical system parameters will be furnished by the Purchaser. | 30 | After | Effective Date |  | No
06xx | 16031 | Generator current transformer secondary excitation characteristic curve | 30 | After | Effective Date |  | No
06xx | 16031 | Generator current transformer ratio correction factor curve | 30 | After | Effective Date |  | No
06xx | 16031 | Generator current transformer thermal rating | 30 | After | Effective Date |  | No
06xx | 16031 | Generator current transformer mechanical rating | 30 | After | Effective Date |  | No
06xx | 16031 | Generator current transformer IEC or ANSI metering and relaying accuracy class | 30 | After | Effective Date |  | No
06xx | 16031 | Generator current transformer secondary resistance at 77.0° F (25° C) | 30 | After | Effective Date |  | No
06xx | 16031 | Generator current transformer phase angle correction factor curves | 30 | After | Effective Date |  | No
06xx | 16031 | Generator current transformer correction factor curves | 30 | After | Effective Date |  | No
05xx | 16031 | Mathematical mode of associated turbine governor, generator, exciter, and AVR | 30 | After | Effective Date |  | No
05xx | 16031 | Hydrogen seal oil diagrams | 90 | After | Effective Date |  | No
05xx | 16031 | Hazardous Area Layout Drawings for all areas where explosive gasses or dusts are introduced by the supplied equipment. | 60 | After | Effective Date |  | Yes
06xx | 16031 | Complete listing of all accessory equipment with instrument ranges and recommended contact set points | 90 | After | Effective Date |  | No
06xx | 16031 | List of all control devices and/or process set points, ranges, and flow quantities | 90 | After | Effective Date |  | No
06xx | 16031 | Listing of accessory equipment to be shipped loose to jobsite | 120 | After | Effective Date |  | No
05xx | 16031 | Piping and Instrument Diagrams | 90 | After | Effective Date |  | No
05xx | 16031 | Drawings of all separately mounted equipment indicating information required for setting, piping, and wiring the items | 60 | After | Effective Date |  | No
05xx | 16031 | Drawings indicating location of all generator junction boxes and electrical accessories requiring embedded conduit in the turbine generator pedestal, including recommended quantities and sizes of conduits into each junction box or piece of equipment | 90 | After | Effective Date |  | No
05xx | 16031 | Drawings indicating the size and location of all generator ground pads | 90 | After | Effective Date |  | No
05xx | 16031 | Drawings indicating electrical connection details to the generator terminals, generator neutral enclosure, and generator current transformers | 90 | After | Effective Date |  | No
05xx | 16031 | Detailed schematic drawings of all electrical control wiring | 90 | After | Effective Date |  | No
05xx | 16031 | All certified drawings required to indicate miscellaneous piping and wiring connections and any other piping and wiring connections not indicated on previous drawings. This shall include piping diagrams as required to indicate manufacturer's requirements for the Purchaser's piping systems. | 90 | After | Effective Date |  | No
05xx | 16031 | Arrangement drawings of all piping and accessories furnished, as required for the Engineer's check of the layout of these items | 90 | After | Effective Date |  | No
05xx | 16031 | Drawings as required to indicate the details of construction and internal wiring of all equipment and equipment components furnished. Detail drawings of standard gauges, instruments, valves, and similar miscellaneous items. | 180 | After | Effective Date |  | No
06xx | 16031 | Generator terminal enclosure outline and loading data | 90 | After | Effective Date |  | No
| 16051 | Electrical Design and Equipment |  |  | .
06xx | 16051 | Certified design data and performance curves | 70 | Before | Shipment |  | Yes or No
05xx | 16051 | Arrangement and fabrication/ erection drawings | 90 | After | Effective Date |  | Yes or No
05xx | 16051 | Detailed set of drawings to include arrangement drawings, one-line and three-line diagrams, metering and relaying diagrams, schematics, instrument door details, nameplate schedule, and bill of materials | 60 | After | Effective Date |  | Yes or No
05xx | 16051 | Final set of above drawings in addition to interconnection wiring diagrams | 21 | After | Purchaser comments on initial drawings |  | Yes or No
05xx | 16051 | Final submittal of as-built drawings | 30 | After | Shipment |  | Yes or No
| 16051 | Relay instruction and service manual including relay curve information | 90 | After | Effective Date |  | Yes or No
06xx | 16051 | Current transformer ratio correction factor and excitation curves | 90 | After | Effective Date |  | Yes or No
06xx | 16051 | Time overcurrent curves for each overload, molded case circuit breaker, and solid-state protective device used | 30 | After | Effective Date |  | Yes or No
05xx | 16051 | I/O database and I/O wiring diagrams |  | Upon | Shipment |  | Yes or No
XXXX | 16051 | Arc Flash Study | 90 | After | Effective Date |  | No
XXXX | 16051 | Short Circuit Sizing Calculations | 90 | After | Effective Date |  | No
XXXX | 16051 | Motor Starting Calculations | 90 | After | Effective Date |  | No
XXXX | 16051 | Relay Setting Calculations | 180 | After | Effective Date |  | No
XXXX | 16051 | Overload Sizing Calculations | 90 | After | Effective Date |  | No
XXXX | 16051 | Cable Ampacity Calculations | 90 | After | Effective Date |  | No
XXXX | 16051 | Circuit List (with format for B&V CARMS input) | 90 | After | Effective Date |  | Yes
XXXX | 16051 | Raceway List | 120 | After | Effective Date |  | Yes
XXXX | 16051 | Lighting Circuit List | 120 | After | Effective Date |  | No
XXXX | 16051 | Lighting Raceway List | 120 | After | Effective Date |  | No
XXXX | 16051 | Cable Tray Loading (weight/meter) | 120 | After | Effective Date |  | No
XXXX | 16051 | Cable Tray Layout Drawings | 120 | After | Effective Date |  | No
XXXX | 16051 | Grounding Installation Drawings for equipment with scope with sufficient detail to confirm code requirements | 120 | After | Effective Date |  | No
XXXX | 16051 | Raceway Composites | 120 | After | Effective Date |  | No
XXXX | 16051 | Instrument Location Drawings | 120 | After | Effective Date |  | No
| 16142 | Generator Neutral Grounding |  |  | .
06xx | 16142 | Bill of Material, Including Quantity, Description, and Part Number |  | Upon | Effective Date |  | Yes or No
06xx | 16142 | Certified design calculations | 30 | After | Effective Date |  | Yes or No
05xx | 16142 | Preliminary outline drawings including overall height, length, width, center of gravity location, and weight | 15 | After | Effective Date |  | Yes or No
05xx | 16142 | Final outline drawings | 60 | After | Effective Date |  | Yes or No
05xx | 16142 | Schematic and wiring diagrams | 60 | After | Effective Date |  | Yes or No
| 16201 | Protective Relaying Panels |  |  | .
05xx | 16201 | Outline drawings including overall height, length, width, center of gravity location, weight and mounting requirements. | 15 | After | Effective Date |  | Yes or No
05xx | 16201 | Schematic diagrams | 30 | After | Effective Date |  | Yes or No
05xx | 16201 | Connection and wiring diagrams | 30 | After | Effective Date |  | Yes or No
05xx | 16201 | Erection drawing | 30 | After | Shipment |  | Yes or No
06xx | 16201 | Relay installation and wiring information | 30 | After | Effective Date |  | Yes or No
05xx | 16201 | Nameplate drawings | 45 | After | Effective Date |  | Yes or No
| 17051 | Control Design and Equipment |  |  | .
05xx | 17051 | PLC power, communications, and grounding wiring diagrams | 90 | After | Effective Date
05xx | 17051 | PLC equipment location and arrangement drawings | 90 | After | Effective Date
05xx | 17051 | PLC I/O wiring diagrams | 120 | After | Effective Date
05xx | 17051 | PLC program printouts for review | 180 | After | Effective Date
05xx | 17051 | PLC external hardwired I/O list | 90 | After | Effective Date
05xx | 17051 | PLC to DCS I/O data interface list (if applicable) | 180 | After | Effective Date
05xx | 17051 | Recommended DCS graphic displays (if applicable) | 180 | After | Effective Date
05xx | 17051 | Complete set of hardcopy printout of all graphic displays for local control (if applicable) | 180 | After | Effective Date
07xx | 17051 | PLC system operation and maintenance instruction manuals |  |  | At equipment shipment
07xx | 17051 | Operator interface system operation and maintenance instruction manuals |  |  | At equipment shipment
| 17051 | Final PLC program printouts |  |  | At equipment shipment
| 17052 | Local Control Panels |  |  | .
05xx | 17052 | Panel outline dimension drawings including overall height, length, width, center of gravity location, and weight. | 15 | After | Effective Date |  | Yes or No
05xx | 17052 | Panel internal arrangement drawings | 30 | After | Effective Date |  | Yes or No
05xx | 17052 | Control panel layout drawings | 30 | After | Effective Date |  | Yes or No
05xx | 17052 | Panel internal wiring diagrams | 60 | After | Effective Date |  | Yes or No
05xx | 17052 | Panel external connection diagrams | 60 | After | Effective Date |  | Yes or No
05xx | 17052 | Panel tubing and piping drawings | 60 | After | Effective Date |  | Yes or No
06xx | 17052 | Panel component cut sheets | 30 | After | Effective Date |  | Yes or No
| 17053 | Subsystem - Programmable Logic Control System |  |  | .
04xx | 17053 | Factory Acceptance Test Procedure | 90 | Before | Test
05xx | 17053 | Outline drawings including overall height, length, width, center of gravity location, and weight. | 30 | After | Effective Date |  | Yes or No
05xx | 17053 | PLC System equipment layout | 30 | After | Effective Date |  | Yes or No
05xx | 17053 | PLC System internal wiring | 45 | After | Effective Date |  | Yes or No
05xx | 17053 | PLC System external connection diagrams | 45 | After | Effective Date |  | Yes or No
05xx | 17053 | PLC external hardwired I/O list | 90 | After | Effective Date
05xx | 17053 | Preliminary PLC to DCS I/O data interface list (if applicable) | 60 | After | Effective Date
05xx | 17053 | Final PLC to DCS I/O data interface list (if applicable) | 180 | After | Effective Date
05xx | 17053 | Preliminary recommended DCS graphic displays (if applicable) | 60 | After | Effective Date
05xx | 17053 | Final recommended DCS graphic displays (if applicable) | 180 | After | Effective Date
05xx | 17053 | Complete set of hardcopy printout of all graphic displays for local control (if applicable) | 180 | After | Effective Date
06xx | 17053 | Complete Bill of Materials for PLC System | 30 | After | Effective Date |  | Yes or No
06xx | 17053 | Hard copy printouts of final PLC application program |  | Upon | Shipment |  | Yes or No
| 19000 | Quality System Requirements |  |  | .
04xx | 19000 | Certification Letter or Certificate of Authorization (copy), if certified by a registered agency, e.g., ASME Certificate of Authorization, ISO Certificate | 30 | After | Effective Date
04xx | 19000 | Subsupplier listing | 5 | Before | Issue of Subsupplier Purchase Order
04xx | 19000 | Notification of inspection/test (for B&V hold/witness points) | 14 | Before | Test/Inspection
04xx | 19000 | Quality Manual, uncontrolled copy | 28 | After | Effective Date
04xx | 19000 | Inspection and test plan with monthly inspection target dates | 28 | After | Effective Date and then monthly thereafter
| E100 | Wiring Methods, Cable and Raceway |  |  | .
05xx | E100 | Supplier Circuit List (with format for B&V CARMS input) Specifier: Include this requirement only if Supplier is designing circuits between equipment. | 90 | After | Effective Date |  | Yes
05xx | E100 | Raceway List Specifier: Include this requirement only if Supplier is designing interconnecting raceway between equipment. | 120 | After | Effective Date |  | Yes
05xx | E100 | Final Lightning Protection Equipment list and commodities quantity, broken down by construction work area. Specifier: Include this requirement only if supplier is designing lightning protection equipment. | 90 | After | Effective Date |  | Yes
| E640 | Low Voltage Induction Motors |  |  | .
05xx | E640 | Motor dimensional drawings | 60 | After | Effective Date |  | No
05xx | E640 | Motor nameplate data | 60 | After | Effective Date |  | No
| E642 | Single-Phase Induction Motors |  |  | .
05xx | E642 | Motor nameplate data | 60 | After | Effective Date |  | Yes or No
05xx | E642 | Motor dimensional drawings | 60 | After | Effective Date |  | Yes or No
| E645 | Electric Actuators |  |  | .
05xx | E645 | Actuator outline diagrams | 30 | After | Effective Date |  | No
05xx | E645 | Wiring diagrams | 30 | After | Effective Date |  | No
| K100 | Instrumentation General Requirements |  |  | .
05xx | K100 | Supplier Instrument List and quantities: Detailed list of instrumentation and control equipment listing manufacturer, model number, range, set point, signal level, etc, broken down by plant construction work area. | 90 | After | Effective Date |  | No
05xx | K100 | Instrument Location Plan Drawings | 90 | After | Effective Date |  | Yes
05xx | K100 | Instrument factory calibration sheets |  | Upon | Shipment of Instruments |  | Yes
05xx | K100 | ISA-format datasheets for all Instruments | 120 | After | Effective Date |  | Yes
| K102 | TEs, TWs Protection Tubes, and Xmtrs |  |  | .
06xx | K102 | PTC 19.3 calculations for steam line TW's vib failure analysis confirming thermowells will not fail in service or during steam blow conditions. | 120 | After | Effective Date |  | Yes
| K120 | Instrument Valves and Instrument Primary Piping-Tubing |  |  | .
05xx | K120 | Instrument Installation Details | 90 | After | Effective Date |  | Yes
05xx | K120 | Sample and Instrument Tubing and fittings BOQ, broken down by construction work area Specifier- only include if Supplier is designing instrument and/or sample tubing. | 120 | After | Effective Date |  | Yes
| Q100 | General Welding Requirements |  |  | .
04xx | Q100 | Welding Procedure Specifications (WPS) with applicable Procedure Qualification Records (PQR) | 60 | Before | Start of Fabrication
04xx | Q100 | Procedures for storing, issuing, and reconditioning of electrodes, wires, and fluxes | 60 | Before | Start of Fabrication
04xx | Q100 | Repair procedures associated with a nonconformance report | 5 | After | Discovery of Repair
04xx | Q100 | Post-weld heat treatment procedures | 60 | Before | Start of Fabrication
04xx | Q100 | Visual inspectors' qualifications and certificates | 60 | Before | Start of Fabrication
04xx | Q100 | Nondestructive examination procedures | 60 | Before | Start of Fabrication
04xx | Q100 | Nonconformance reports | 5 | After | Discovery of Nonconf.
04xx | Q100 | Radiographs or UT reports | 14 | After | Fabrication Completion
| Q110 | Welding of 9Cr-1Mo-V (Grade 91) and 9Cr-2W (Grade 92) Materials |  |  | .
04xx | Q110 | Procedures for storing, issuing, and reconditioning of electrodes, wires, and fluxes | 60 | Before | Start of Fabrication
04xx | Q110 | Preheat and bakeout procedures | 60 | Before | Start of Fabrication
04xx | Q110 | Filler material CMTRs | 60 | Before | Start of Fabrication
04xx | Q110 | ASME B31.1 shop fabricated piping spools P91/P92 documentation records | 21 | Before | Shipment
| Q121 | General Structural Welding Requirements |  |  | .
04xx | Q121 | Welding Procedure Specifications (WPS) with applicable Procedure Qualification Records (PQR) | 60 | Before | Start of Fabrication
04xx | Q121 | Procedures for storing, issuing, and reconditioning of electrodes, wires, and fluxes | 60 | Before | Start of Fabrication
04xx | Q121 | Repair procedures associated with a nonconformance report | 5 | After | Discovery of Repair
04xx | Q121 | Visual inspectors' qualifications and certificates | 60 | Before | Start of Fabrication
04xx | Q121 | Nonconformance reports | 5 | After | Discovery of Nonconf.
04xx | Q121 | Radiographs or UT reports | 14 | After | Fabrication Completion
| Q126 | General Structural Welding Requirements |  |  | .
04xx | Q126 | Welding Procedure Specifications (WPS) with applicable Procedure Qualification Records (PQR) | 60 | Before | Start of Fabrication
04xx | Q126 | Procedures for storing, issuing, and reconditioning of electrodes, wires, and fluxes | 60 | Before | Start of Fabrication
04xx | Q126 | Repair procedures associated with a nonconformance report | 5 | After | Discovery of Repair
04xx | Q126 | Visual inspectors' qualifications and certificates | 60 | Before | Start of Fabrication
04xx | Q126 | Nonconformance reports | 5 | After | Discovery of Nonconf.
04xx | Q126 | Radiographs or UT reports | 14 | After | Fabrication Completion
| Q301 | Manufacturer's Standard Coating |  |  | .
06xx | Q301 | Shop drawings that identify shop-applied coating systems | 30 | Before | Start of Fabrication |  | No
06xx | Q301 | Manufacturer's product data sheets, to include DFT per coat, number of coats and total coating system DFT | 30 | After | Release to Proceed |  | No
| Q302 | Purchaser Specified Shop Coating |  |  | .
06xx | Q302 | Manufacturer's product data sheets | 30 | After | Release to Proceed |  | No
06xx | Q302 | Manufacturer's color cards | 30 | After | Release to Proceed |  | No
06xx | Q302 | Manufacturer's surface preparation and coating application procedures. Include manufacturer's construction standards and recommended practices for surface contamination testing, crack and joint treatment, edge treatment, coating penetration and termination. | 30 | After | Release to Proceed |  | No
04xx | Q302 | Manufacturer's certification of the coating applicator | 30 | After | Release to Proceed |  | No
04xx | Q302 | Applicator's experience record | 30 | After | Release to Proceed |  | No
04xx | Q302 | Manufacturer's approval of surface condition prior to coating application | 10 | After | Release to Proceed |  | No
04xx | Q302 | Applicator's inspection and test reports | 7 | After | Test/Inspection |  | No
04xx | Q302 | Manufacturer's field representative inspection and test report | 7 | After | Test/Inspection |  | No
| Q303 | Interior Coatings and Linings |  |  | .
06xx | Q303 | Manufacturer's product data sheets | 30 | After | Release to Proceed |  | No
06xx | Q303 | Applicator's blast media data sheets | 30 | After | Release to Proceed
06xx | Q303 | Manufacturer's surface preparation and coating application procedures. Include manufacturer's construction standards and recommended practices for surface contamination testing, crack and joint treatment, edge treatment, coating penetration and termination. | 30 | After | Release to Proceed |  | No
04xx | Q303 | Manufacturer's certification of the coating applicator | 30 | After | Release to Proceed |  | No
04xx | Q303 | Applicator's experience record | 30 | After | Release to Proceed |  | No
04xx | Q303 | Applicator's approval of manufacturer's surface preparation and coating application procedures | 30 | After | Release to Proceed |  | No
04xx | Q303 | Manufacturer's approval of surface condition prior to coating application | 10 | After | Release to Proceed |  | No
04xx | Q303 | Applicator's inspection and test reports | 7 | After | Test/Inspection |  | No
04xx | Q303 | Manufacturer's field representative inspection and test report | 7 | After | Test/Inspection |  | No
| Q400 | General Equipment Requirements |  |  | .
03xx | Q400 | Shipment Plan providing details of field assembly work required as described in the Supplier's proposal. | 30 | After | Effective Date |  | No

## Bid Submittals
JEA |  | Request for Proposal
418692.67.9100 | Power Island Equipment | 2024-09-09
Technical input to 00300.6 Bid Submittals Required with Quotation
Reference Document | Submittal Item | Yes/No
Bid Submittals
15272 | Bypass Valves | .
15272 | Manufacturer's control valve specification data sheets.
15511 | Heat Recovery Steam Generator | .
15511 | Listing of Work subcontracted to other Suppliers.
15511 | Listing of Subsuppliers used.
15511 | Bidder's preliminary engineering schedule.
15511 | Bidder's procurement/production/shipping schedule.
15511 | List of similar units in construction or operation
15511 | Preliminary P&IDs (high/intermediate/low pressure systems, superheater/reheater systems, flue gas, burner, SCR/ammonia flow control unit, ammonia injection grid, blowdown, etc.)
15511 | Heating surface data for evaporator, economizer, reheater, superheater, etc. bundles.
15511 | Equipment arrangement drawings from CT outlet expansion joint to outlet of stack outlet- elevation, side, plan, etc.
15511 | Equipment arrangement drawings: duct burner, fuel skid, stair towers, ammonia injection system (SCR), HRSG pressure parts, stack damper, etc.
15511 | Provide drawings of the proposed manway doors, material specifications (doors and gaskets), installation instructions, experience list with the proposed design, specifically with cycling HRSGs.
15511 | Extent of piping fabrication performed off site.
15511 | Number of tube welds and header welds in HP section of HRSG by size/sch.
15511 | Number of tube welds and header welds in IP section of HRSG by size/sch.
15511 | Number of tube welds and header welds in Reheat section of HRSG by size/sch.
15511 | Number of tube welds and header welds in LP section of HRSG by size/sch.
15511 | Number of field welds for components, by size/sch, composed of alloy materials such as P/T11, P/T22, P/T91, etc.
15511 | Number of tube welds and header welds in BOP piping.
15511 | Estimated structural steel quantity (tons).
15511 | Preliminary Electrical Load List, including equipment tagging, equipment description, voltage, and the rated and operating electrical loads.
15561 | Steam Turbine | .
15561 | Cycle Heat balance diagrams.
15561 | Exhaust correction curves
15561 | Startup curves for hot, warm, and cold startups indicating flow, temperature, time, and other parameters for normal startups and loading rate curve.
15561 | Turbine overall length, width, height, and shaft center line to floor line dimension.
15561 | Table of weights and dimensions indicating assembled weights and dimensions of major components, weights to be handled during erection, and weights to be handled during overhaul.
15561 | List of special tools, including a description and quantity of each item and whether it is required for erection and/or maintenance.
15561 | Complete list of recommended spare parts.
15561 | Description of required sectional shipments if equipment cannot be completely factory assembled.
15561 | Information on the TSI system
15561 | Description of manufacturer's lagging design.
15561 | Complete description of the lube oil piping arrangement.
15561 | Complete data on steam purity requirements.
15561 | List of reference plants with similar turbines under construction or in operation.
15561 | Listing of suppliers and their manufacturing locations.
15561 | Bidder's preliminary engineering schedule.
15561 | Bidder's preliminary procurement/production/shipping schedule.
15561 | Description of data link provided to Purchaser's DCS.
15561 | Description of automation equipment for automatic run-up of turbine.
15561 | Description of turbine rotor stress monitoring system.
15561 | Description of turning gear.
15561 | Description of field assembly work required and estimated manpower requirements for erection of equipment.
15562 | Combustion Turbine | .
15562 | Combustion turbine generator performance curves
15562 | Combustion turbine heat rate, exhaust flow, and exhaust temperature curves versus load, showing the effect of inlet guide vane (IGV) control
15562 | Compressor inlet temperature correction curves for heat rate, capacity, exhaust temperature, and mass flow
15562 | NOx injection water (or steam) correction curves for effects on heat rate, capacity, exhaust temperature, mass flow, and emissions for varying amounts of water (or steam) injection for NOx control.
15562 | NOx control water (or steam) injection requirement versus combustion turbine load curve for all specified fuels at various compressor inlet temperatures.
15562 | Curves indicating the effect of inlet anti-icing on output and heat rate.
15562 | NOx and CO emission level versus load for all specified fuels.
15562 | CO, UHC, and VOC emission levels versus water (or steam) injection rate curve.
15562 | Inlet pressure drop correction data.
15562 | Exhaust pressure drop correction data.
15562 | Humidity correction data.
15562 | Atmospheric pressure (or altitude) correction curves.
15562 | Estimated output, heat rate, exhaust flow, and exhaust temperature degradation versus fired hours curves from initial startup through second major overhaul for firing each specified fuel.
15562 | Curves showing recovery effects of compressor washing for output, heat rate, exhaust flow, and exhaust temperature.
15562 | Detailed description of starting system.
15562 | List of Drawings to be provided during project execution and schedule of drawing submittals.
15562 | Preliminary/typical general arrangement Drawings showing the combustion turbine generator unit(s), inlet filter(s), exhaust stack(s), all associated compartments/enclosures/skids, starter unit, transformers, and radiators. A vertical section shall be included showing the complete installed unit including crane minimum hook height and capacity.
15562 | Control system architecture drawing identifying all microprocessors, operator interface devices, and interconnecting data highways.
15562 | Preliminary/typical one-line diagrams of generator electrical system, including ac and dc auxiliary electric system. One-line diagrams shall include all auxiliary load data and proposed metering and protective relaying.
15562 | A complete description of all equipment proposed, together with supportive data.
15562 | Preliminary Engineering Schedule.
15562 | Preliminary Procurement/Production/Shipping Schedule.
15562 | Shipping methods and erection criteria and requirements.
15562 | Description of manufacturer's performance estimating procedure, including correction procedures for differing altitudes, ambient temperatures, part loads, NOx emissions, water (or steam) injection rates, and IGV control.
15562 | Information on technical assistance provided during erection and commissioning.
15562 | Description of proposed classroom instruction for operations and maintenance training.
15562 | Description and drawing of lay-down space requirements with area defined.
15562 | Description and drawing of additional maintenance area required in addition to the lay-down space defined.
15562 | Priced lists of recommended spare parts.
15562 | List of Startup And Commissioning Spare Parts furnished with the equipment.
15562 | List of all maintenance tools/special tools furnished with the equipment.
15562 | Discussion of emission level changes with increasing operating hours.
15562 | Provide estimated hours to erect proposed combustion turbine generator unit, broken down by craft.
15562 | Description of all field assembly/erection required. Any item not described will be assumed to be fully factory finished.
15562 | Description of factory testing program for furnished equipment.
15562 | Description of the extent of nondestructive testing of unit components, including the casing, rotor forgings, shafts, machine journals, and other major components.
15562 | Description of compressor and turbine blade coatings.
15562 | Description of compressor and turbine blade material and method for securing to rotor and casing.
15562 | Description of burners, ignitors, and combustion system for the proposed combustion system including cross-section Drawings.
15562 | Description of flame safety and combustion control systems.
15562 | Description of arrangements to accommodate thermal expansion of the casings.
15562 | Description of thermal treatment for turbine casings, rotors, and shaft to minimize possibility of distortion occurring in operation.
15562 | List of borescope port locations.
15562 | Description of methods and equipment required for field balancing.
15562 | Description of liquid and gaseous fuel systems and balance-of-plant support/interface requirements.
15562 | Liquid and gaseous fuel requirements (temperature, pressure, minimum required fuel superheat, purity, viscosity, minimum heating value, etc.).
15562 | Description of on-line automatic fuel changeover system including liquid fuel purge system, compartment cooling, etc.
15562 | Description of combustion turbine generator lubricating system, including lubrication schedules, types, quantities, filters, maintenance intervals, etc.
15562 | Description of backup or redundancy features provided in lube oil system and seal oil system.
15562 | Description of the combustion turbine generator lube oil cooling system.
15562 | Description of turning gear system, including statement of effect of long-term operation of turning gear.
15562 | Description of manual system for rotating the turbine and generator shafts.
15562 | Description of diverter damper, including listing of existing installations.
15562 | Exhaust stack exit velocity data in feet per second (meters per second) for each specified performance condition.
15562 | Descriptive information on the combustion turbine control system, including a description of all local and remote control functions and local and remote operator interface functions, redundancy, and a list of sensors furnished (transducers, vibration detectors, thermocouples, RTDs, etc.).
15562 | Description of emergency trip system, including fuel shutoff control.
15562 | Description of combustion turbine automatic generation control (AGC) system and capabilities.
15562 | Description of fire protection and detection equipment with a discussion on compliance with NFPA requirements.
15562 | Description of unit enclosures and noise attenuation features.
15562 | Description of procedure for enclosure disassembly in large sections to accommodate major maintenance.
15562 | Description and arrangement Drawings of the acoustical barrier system for noise attenuation, if required.
15562 | Description of compressor water wash equipment and cleaning chemical requirements.
15562 | Description of inlet air filtration system.
15562 | Description of inlet anti-icing system, including conditions under which it is required for operation.
15562 | Description of starting system with associated detailed drawings.
15562 | Description of water (or steam) injection/NOx reduction control system, including the combustion turbine manufacturer's operating experience with water (or steam) injection for the combustion turbine model proposed, pressure, temperature, and purity requirements for injection for NOx control.
15562 | Water quality and blowdown information for the evaporative cooler system.
15562 | Description of proposed insulation and lagging systems.
15562 | Description of enclosure/compartment HVAC system, including design temperatures.
15562 | Description of overspeed protection system.
15562 | Detailed description of unit startup event sequence, including times, auxiliary power requirements, amperage versus time curve, etc. (separately address "normal" and "fast" starts).
15562 | Description of proposed shutdown corrosion protection system
15562 | Description of planned future upgrades (capacity increases) to the unit(s) proposed and effects these upgrades will have on the electrical equipment specified.
15562 | Complete current experience listings for the combustion turbine generator model proposed indicating the following information as a minimum:
15562 | Recommended maintenance practices and procedures, including frequency of routine inspection intervals and required parts. Include man-hours required to complete the combustion inspection, hot gas path inspection, and the first major overhaul.
15562 | Complete description of the data link hardware, software, and communications protocol for the interface to the Purchaser's DCS.
15562 | Complete description of the data link hardware, software, and communications protocol for the interface to the Purchaser's SCADA system.
15562 | Description of any special control system grounding requirements.
15562 | Complete description of the proposed Turbine Generator Supervisory System including equipment provided, list of sensors furnished, and operator interface functions.
15562 | Complete description of the proposed Vibration Monitoring System including equipment provided, list of sensors furnished, and operator interface functions.
15562 | Water quality and blowdown information for the evaporative cooler system.
15562 | List of codes and standards used in design of all equipment including version or issue date.
16031 | Cylindrical Rotor Generators | .
16031 | Reactive capability curve to indicate generator capability at various power factors.
16031 | Generator saturation curve.
16031 | Generator "Vee" curves.
16031 | Drawings of recommended method of stator erection.
16031 | Generator drawing with overall length, width, and height.
16031 | Generator drawing with exciter or collector's overall length, width, and height.
16031 | Generator drawing with excitation cubicle's overall length, width, and height.
16031 | Generator drawing with rotor removal clearance (straight and askew).
16031 | Generator drawing with control cabinet's overall length, width, and height.
16031 | Generator drawing with supervisory cabinet's overall length, width, and height.
16031 | Complete list of required maintenance tools. The listing shall include a complete description and quantity of each item.
16031 | Equipment storage requirements, including inside or outside requirements, requirements for controlled temperature or humidity, etc.
16031 | Complete list of necessary special tools. The listing shall provide a complete description and quantity of each item, including a discussion or designation of particular items required for erection and/or maintenance.
16031 | Complete list of recommended spare parts.
16031 | Description and listing of major generator assemblies for shipment.
16031 | Information describing coating systems for equipment.
16031 | One uncontrolled copy of bidder's Quality Assurance Program.
16031 | Complete information on the generator supervisory instrumentation system, including a bill of material.
16031 | Detailed listing of alarm contacts available and recommended alarms for connection to DCS, including unit prices for additions or deductions.
16031 | Detailed listing of instrumentation furnished.
16031 | Complete description of cable requirements, including the cable constructions, for all equipment furnished.
16031 | Complete description of any voltage level separation requirements for raceway or special cable shielding requirements for all equipment furnished.
16031 | Complete description of the lube oil piping arrangement.
16031 | Complete list of other plants where the manufacturer has duplicate, or near duplicate, generators under construction or in operation.
16031 | Listing of Work subcontracted to other Suppliers.
16031 | Listing of Subsuppliers and Suppliers used.
16031 | Bidder's preliminary engineering schedule.
16031 | Bidder's procurement/production/shipping schedule.
16031 | Complete description of excitation system.
16031 | Complete description of generator core monitor system (if specified).
16031 | Generator maximum allowable temperature of cold coolant generator temperature rise of gas and liquid.
16031 | Generator maximum allowable temperature for armature winding, field winding, core, and mechanical parts in contact with or adjacent to armature winding insulation; and collector rings, brushes, and brush holders.
16031 | Detailed description of the brushless exciter (if specified).
16031 | Maximum allowable temperature of cooling air and temperature rise of cooling air.
16051 | Electrical Design and Equipment | .
16051 | Bill of quantities for all items.
16051 | Dimensional outline drawings.
16051 | One-line diagrams showing equipment provided and equipment layout.
16051 | A list of special tools included in the proposal. The listing shall include a complete description and quantity of each item.
16051 | Equipment storage requirements, including inside or outside requirements, requirements for controlled temperature or humidity, etc.
16051 | A complete priced recommended maintenance and spare parts list.
16051 | List of components with lead times longer than 30 days that will be ordered and shipped from another manufacturing facility for assembly in the final assembly plant.
16051 | List origin of major components, factory manufactured or assembled.
16051 | Wiring philosophy and typical wiring diagrams for wiring to I/O blocks in the factory.
16142 | Generator Neutral Grounding | .
16142 | Preliminary outline drawing showing "not to exceed" dimensions, weights, and oil quantity.
16142 | Manufacturer's standard shipping, handling, and installation pamphlets.
16142 | Manufacturer's standard informational brochures.
16201 | Protective Relaying Panels | .
16201 | Bill of quantities for protective relay panels.
16201 | Manufacturer's standard shipping, handling, and installation pamphlets.
16201 | Manufacturer's standard informational brochures.
16201 | Manufacturer's standard raceway.
16201 | Bill of quantities for protective relay panels.
17052 | Local Control Panels | .
17052 | Panel dimensions.
17052 | Panel weight.
17052 | Proposed panel layout.
17052 | Recommended spare parts list.
17053 | Subsystem - Programmable Logic Control System | .
17053 | Description of proposed PLC equipment, including manufacturer, model, memory type and capacity, types and quantities of I/O modules provided, and preliminary PLC system architecture and layout.
17053 | Description of proposed optional programming unit, if required, including manufacturer, model, memory and disk capacities, and any accessories supplied. Also, describe the proposed programming software, including manufacturer, model, features, and capabilities.
17053 | Description of proposed optional interface to plant DCS, if required, including communication standard, protocol, and media.
17053 | Description of proposed optional CRT-based graphical operator interface, if required, including manufacturer, model, memory and disk capacities, MMI software type, MMI features and capabilities, and proposed operator displays.
17053 | Preliminary I/O list.
17053 | Total system power consumption.
E645 | Electric Actuators | .
E645 | List of all codes and standards used in design, construction, and testing of electric actuators, including version and issue date.
E645 | Manufacturer and model of all proposed electric actuators.

## Tech Fill In
JEA |  | Request for Proposal
418692.67.9100 | Power Island Equipment | 2024-09-09
Technical input to 00300.7 Technical Fill-In Data Required with Quotation
Reference Document | Submittal Item | Tech Fill-In Data
Technical Fill-In Data
01100 | Equivalent Availability Factor
01100 | Equivalent Forced Outage Rate
11508 | Ammonia Vaporization and Injection System
11508 | Ammonia System Supplier | .
11508 | Dimensions of skid, in. (mm)
11508 | Ammonia area monitors
11508 | Number
11508 | Manufacturer
11508 | Ammonia Vaporization (Electric / FGR)
11508 | Vaporizer manufacturer
11508 | Dilution air fans, number
11508 | Ammonia Vaporization and Injection System, maximum power (kW)
11508 | Vaporizer Turndown, percent
11508 | Vaporizer outlet temperature, °F (°C)
11508 | Atomizing nozzle type
11508 | Atomizing medium
11508 | Ammonia Injection Grid piping material
11508 | Number of independently adjustable ammonia injection zones
11508 | Nozzle matrix
11508 | Nozzles manufacturer
11508 | Nozzle material
11508 | Injection grid branch flow measurement device type
11508 | Describe methods used to measure NH3 distribution
11508 | Describe provisions for optimizing reagent distribution
11508 | List of installations where this design has been used recently
11508 | Distance between injection grid and first catalyst layer, in. (mm)
11508 | Maximum ammonia supply capacity of system, lb/h (kg/h)
11508 | Minimum ammonia supply capability of system, lb/h (kg/h)
13125 | Pre-Manufactured Metal Equipment Building
13125 | Electrical/Control Building
13125 | Item
13125 | Description
13125 | Manufacturer
13125 | Location of manufacturer
13125 | Standard for manufacturing and testing
13125 | Design permissible loading, lb/ft2 (kg/m2)
13125 | Floor
13125 | Roof
13125 | Wind
13125 | Dimensions, inches (mm)
13125 | Height
13125 | Depth
13125 | Length
13125 | Total weight, lb (kg)
13125 | Lighting
13125 | Lighting fixture type
13125 | Switch type
13125 | Receptacle type
13125 | Contactor type
15272 | Bypass Valves
15272 | Bidder's Name
15272 | Manufacturer's name
15272 | Manufacturer's model/type
15272 | Body
15272 | Type
15272 | Rating, ANSI pressure class
15272 | Size, in. (mm)
15272 | Inlet
15272 | Outlet
15272 | Body material
15272 | Maximum recommended valve opening for continuous operation, percent of travel
15272 | Valve sizing coefficient | .
15272 | Maximum
15272 | Minimum
15272 | Materials | .
15272 | Plug
15272 | Seat or seat ring
15272 | Cage or guides
15272 | Stem/shaft
15272 | Disk
15272 | Packing
15272 | Operator | .
15272 | Type
15272 | Manufacturer
15272 | Size
15272 | Control valves air usage
15272 | Travel time (without speed control device) | .
15272 | Full open to full closed
15272 | Full closed to full open
15272 | Total weight (valve, operator, and all accessories on the valve)
15272 | Maximum equivalent "A" weighted sound pressure level, area measured 3 feet (1 m) downstream of the valve outlet and 3 feet (1 m) from the pipe surface, dBA to a reference of 20 micropascals
15272 | Accessories | .
15272 | Positioners | .
15272 | Manufacturer
15272 | Model
15272 | Solenoid valves | .
15272 | Manufacturer
15272 | Model
15272 | Current/pneumatic converters | .
15272 | Manufacturer
15272 | Model
15272 | Position transmitters | .
15272 | Manufacturer
15272 | Model
15272 | Limit switches | .
15272 | Manufacturer
15272 | Model
15272 | Diffusers | .
15272 | Manufacturer
15272 | Model
15272 | Silencers | .
15272 | Manufacturer
15272 | Model
15272 | Volume chambers | .
15272 | Manufacturer
15272 | Model
15511 | Heat Recovery Steam Generator
15511 | Total weight empty, lb
15511 | Time required to bring HRSG from cold condition to design output condition, min.
15511 | Seismic design
15511 | Average far field sound emissions with combustion turbine operating at rated megawatt load when measured at a distance of 400 ft (122 m) from base of HRSG, dBA/dBC
15511 | Conditions at high-pressure superheater outlet | .
15511 | Steam flow, lb/h
15511 | Steam temperature, F
15511 | Steam pressure, psia
15511 | Conditions at intermediate-pressure superheater outlet | .
15511 | Steam flow, lb/h
15511 | Steam temperature, F
15511 | Steam pressure, psia
15511 | Conditions at low-pressure superheater outlet | .
15511 | Steam flow, lb/h
15511 | Steam temperature, F
15511 | Steam pressure, psia
15511 | Conditions at reheater outlet | .
15511 | Steam flow, lb/h
15511 | Steam temperature, F
15511 | Steam pressure, psia
15511 | Conditions at LP drum water outlet | .
15511 | Feedwater flow, gpm
15511 | Feedwater temperature, F
15511 | Feedwater pressure, psig
15511 | Conditions at high-pressure economizer inlet | .
15511 | Feedwater flow, gpm
15511 | Feedwater temperature, F
15511 | Feedwater pressure, psig
15511 | Conditions at intermediate-pressure economizer inlet | .
15511 | Feedwater flow, gpm
15511 | Feedwater temperature, F
15511 | Feedwater pressure, psig
15511 | Conditions at low-pressure economizer inlet | .
15511 | Condensate flow, gpm
15511 | Condensate temperature, F
15511 | Condensate pressure, psig
15511 | HP Attemperator spray water flow, gpm
15511 | IP Attemperator spray water flow, gpm
15511 | Minimum stack temperature, F
15511 | Maximum gas pressure drop turbine exhaust to stack, outlet, in. w(g)
15511 | Manlift manufacturer
15511 | Manlift capacity, people
15511 | Duct burners | .
15511 | Manufacturer
15511 | Design heat input, Btu/h
15511 | Maximum heat input, Btu/h
15511 | Distance from burner flame tip to next heat transfer surface (at maximum duct burner firing rate), ft (m)
15511 | Ignitor type
15511 | Burner turndown ratio
15511 | Minimum firing capability, percent of design
15511 | Number of burner elements
15511 | Fuel train | .
15511 | Pressure regulating valve | .
15511 | Manufacturer
15511 | Size
15511 | Type No.
15511 | Fuel block and bleed valves | .
15511 | Manufacturer
15511 | Size
15511 | Type No.
15511 | Required inlet fuel pressure, psig
15511 | Fuel gas flow rate (maximum), lb/h
15511 | Casing | .
15511 | Casing material (referenced standard and grade)
15511 | Casing thickness, in.
15511 | Internal insulation | .
15511 | Material (referenced standard and grade)
15511 | Thickness, in.
15511 | Internal liner | .
15511 | Material (referenced standard and grade)
15511 | Thickness, in.
15511 | Casing design pressure, in w(g)
15511 | Expansion joints | .
15511 | Manufacturer
15511 | Location
15511 | Length, ft-in.
15511 | Width, ft-in.
15511 | Height, ft-in.
15511 | Installed weight, lb
15511 | Design pressure, in. w(g)
15511 | Design temperature, F
15511 | Materials (ASTM Standard and grade) | .
15511 | Belt
15511 | Insulation pillow
15511 | Insulation fill
15511 | Frame
15511 | Liner
15511 | Safety shroud
15511 | Bolting
15511 | Stack Data | /
15511 | Stack height, ft-in. | /
15511 | Stack type (round or rectangular) | /
15511 | Cross-sectional dimensions, L x W, ft-in. | /
15511 | Wall design, single or dual | /
15511 | Primary wall material | /
15511 | Primary wall thickness, in. | /
15511 | Foundation anchor bolts requirements | .
15511 | Number
15511 | Type
15511 | Diameter, in.
15511 | Required projection above foundation, in.
15511 | Quantity of test ports provided
15511 | Diameter of test ports provided, in. | .
15511 | Location of platforms provided
15511 | Size of platforms provided, width, ft-in
15511 | Design minimum exhaust gas temperature, F
15511 | Design maximum exhaust gas temperature, F | .
15511 | Exhaust stack emissions limits (see 15511.1.4)
15511 | NOx, ppmvd at 15 percent O2
15511 | CO, ppmvd at 15 percent O2
15511 | Ammonia, ppmvd at 15 percent O2
15511 | VOC, lb/h | .
15511 | Particulate, PM10 lb/hr
15511 | Supplier furnished materials and associated installation quantities | .
15511 | Large Bore (>=2 ½” in diameter) Alloy Pipe, lf
15511 | Structural Steel, tons (Note 2)
15511 | Casing, tons
15511 | Ductwork, tons (Note 3)
15511 | Casing/Ductwork Field Seal Welding, lf (Note 4)
15511 | Platform and Stairs, tons
15511 | Platform and Stairs, pieces
15511 | Modules/Tube Bundles, each
15511 | Modules/Tube Bundles (maximum weight), tons
15511 | Drum Enclosures, pieces
15511 | Drum Enclosures, sf
15511 | Drums & Internals, pieces
15511 | Drums & Internals (maximum weight), tons
15511 | Duct Firing & Control Systems, each
15511 | Off Base Skids & Miscellaneous Equipment, each
15511 | SCR Catalyst, pieces
15511 | Technical Assistance Time, hours
15511 | Notes | .
15511 | 1. Average Diameter for large bore pipe welds is the sum of the diameters for each individual large bore welds divided by the total number of large bore welds. | .
15511 | 2. Structural Steel includes structural members, only, not fasteners, shims, gussets, etc. | .
15511 | 3. Ductwork includes expansion joints, but not fasteners, shims, & gussets. | .
15511 | 4. Casing/Ductwork Field Seal Welding includes expansion joints. | .
15511 | Seal welding is defined as the number of lineal feet of weld placed multiplied by the number of sides from which the weld must be placed. Thus, a seal weld that must be placed from both the inside and outside is equal to the length of the weld multiplied by two (2). | .
15511 | PWHT = post weld heat treatment | .
15561 | Steam Turbine
15561 | Supplementary steam requirements for sealing turbine at low load operation during startup and shutdown
15561 | Flow, lb/h (kg/h)
15561 | Temperature, °F (°C)
15561 | Pressure, psi (kPa)
15561 | Total turbine generator moment of inertia, WK2 (MR2)
15561 | Lubricating Oil System
15561 | Quantity of cooling water required to each cooler at design inlet temperature, gpm (L/min)
15561 | Maximum cooling water temperature for unrestricted operation with design water flow to both coolers (simultaneous operation), °F (°C)