Date: 12/04/2024

TO:		The Contractor

FROM:		System Protection & Control Projects 20413

SUBJECT:	Technical Specifications for Normandy APSTF Project

# PROJECT OVERVIEW

This is a general specification that covers the work requirements for Normandy APSTF Project. Use this document in conjunction with the Cable Schedule, Wiring Diagrams, and other associated schematics/documentation that is given by JEA.

# SCOPE OF WORK

JEA System Protection & Control Projects 20413 (SPCP) is requesting the Contractor to install twenty-nine (29) Control Panels. Decommission and demolish existing Relay Control panels. Pull cable from yard equipment to control house, temporary cables terminations between new and old control house as well as removal at project completion, set temporary termination blocks on wall mount for temporary cables between houses, panel to panel and make terminations inside de-energized relay panels, and remove old cables from yard equipment to control house. Fabrication, procurement, and installation of temporary cable termination racks (including terminal blocks) as specified in the Connection Diagrams (NMC596 & NMC597). Run communication cable (coaxial, Ethernet & fiber). Move or Relocate any interfering objects (furniture, boxes) prior to beginning work.

# SITE

All work shall be performed at Normandy Substation (9801 Crystal Spring Road, Jacksonville, Fl. 32221).

# JEA POINT OF CONTACT & DEPARTMENT

JEA point of contact and department for this work is:

Derek Horn

System Protection & Control Projects 20413

JEA HQ, 4th Floor

225 N Pearl Street

Jacksonville, Florida 32202

Cell: (772) 940-9106

hornd@jea.com

# SCHEDULE OF WORK

The Contractor shall mobilize after the issuance of Purchase Order (PO) from JEA. The Contractor is to note that this work shall be performed in phases dependent upon electrical outages granted by JEA’s System Operations Control Center (SOCC). Therefore, once the outage has been granted by SOCC, The Contractor should have the ability to mobilize within 48-hour notice from JEA Project Manager. Once, the granted outage work has been completed The Contractor maybe asked to demobilize until the next outage has been granted.  The Contractor shall follow Substation Construction Documents to determine the sequence of work.

JEA has Electric System Security concerns, which require that this Work be completed on time. Therefore, time is of the essence.

# SEQUENCE OF WORK

The Contractor shall provide all labor in order to have an orderly progression of this Work. The Contractor will be required to coordinate the Work Schedule with JEA SPCP department and the point of contact listed above. The Contractor shall be responsible for all work coordination, timing, sequencing, and scheduling that is necessary to assure timely completion.  Refer to all documentation to get familiarized with the sequence of this work.

# SUBSTATION ACCESS AND SECURITY

Normandy substation is classified as a NERC CIP Medium site. Therefore, JEA Project        Representative will provide for an onsite Security Guard that will be available for throughout the duration of this work, and when Contractor has on-side activities. The Security Guard shall be responsible for escorting and provide control house, and site access to the Contractor.

### CABLE SCHEDULE

  - The Contractor shall pull all cables as listed in the Cable Schedule. All control cable, Ethernet cable, coaxial, and fiber will be provided by JEA except cables from AC/DC source panels. The Contractor shall be responsible for providing these cables.

  - The Contractor shall pull all cable as listed in the Cable Schedule.

  - The cable should have sufficient slack such that they can be terminated to the new Relay Controls Panels and ample cable for making terminations. The cable should have enough slack to reach the floor of the panel and back to the top of control panel.

  - The Contractor shall leave enough slack in the cable to accommodate for any changes to the Control Panel(s) layout inside the control house.

  - Cable lengths listed in the Cable Schedule are approximate. The Contractor shall be responsible of all cable length prior to cutting.

  - The Contractor is responsible for providing the Owner with accurate “As Built” revision of the Cable Schedule.

  - The Contractor will be responsible for labeling all cables as listed in the Cable Schedule.

  - The contractor shall be responsible for labelling, stripping and installing lugs on the cable on equipment end.

  - When running the new cables from the yard to the control house, Contractor shall

provide a method to separate the new cable from the existing cables in the cable trench to facilitate cable removal by The Contractor.

### TERMINATIONS

  - The Contractor shall be responsible for all terminations into the new de-energized control panels. The Contractor shall include cost of terminating twenty – nine (29) JEA Standard cabinet style relay control panels.

  - Fabrication, procurement, and installation of temporary cable termination racks (including terminal blocks) as specified in the Connection Diagrams (NMC596 & NMC597).

  - The Contractor shall NOT do any terminations into any energized control panels.

  - Ethernet cable, coaxial, and fiber cables will be provided by JEA and shall be run by the contractor before the first (1st) outage.

  - All fiber cable terminations shall be “ST” unless otherwise specified.

  - The Contractor shall be responsible for running and terminating all AC/DC cables from AC/DC load centers to the panels.

### SPLICES

  - All run of control and instrument cable shall be continuous. Splices in control cable shall NOT be permitted.

### LABELING OF CABLE

The Contractor shall install all cables mentioned in the cable schedule and pull list as a part of this work. This shall require that the Contractor perform each of the following:

  - All cables are to be labeled:

- At both ends.

- When entering and leave the cable trench.

- Where exiting station electrical equipment, to include all AC/DC power panels, power circuit breakers, junction boxes, etc.

  - Cable identification tags will be attached to the cable in a manner approved by JEA Project point of contact. The Contractor shall provide corrosion resistant tags for the cables. For exterior application plastic cable ties shall not be permitted.

  - Outdoor cable identification tags shall be ½” wide stainless steel, Dymo M1011 system, unless otherwise approved by the Project Representative. Indoor cable identification tags shall be RhinoPRO ½” flexible nylon labels – black on white, Manufacturer part # 18488, unless otherwise approved by the Project Representative. Indoor labels shall be secure with two plastic ties.

  - All cable identification tags will have the appropriate cable number clearly stamped in no less than ¼” high characters. Cable names are specified on the Cable Schedule attached to these Specifications.

### MATERIALS PICK UP

  - The Contractor shall be responsible to pick up cable reels from other JEA substations or various JEA Storerooms.

  - The Contractor shall be responsible for providing equipment and labor to pick up cable reels from above mentioned location and bring them to the site at Normandy substation.

  - The Contractor shall be responsible to drop unused cable/cable reels to JEA storeroom, location to be provided later.

### CONTROL PANELS

Follow Substation Normandy APSTF Project Construction Guidelines and Instructions documents for Control Panel placement sequencing.  Work sequence shall be as follows:

  - JEA SPC tech will inform JEA SPCP Project Manager upon completion of the relay panel de-termination.

  - JEA SPCP project representative will then give The Contractor 48 hour notice to mobilize and commence their work of removing existing control panels which were de-terminated in 6.1

  - The Contractor will be responsible for removing existing de-terminated cable from the existing control panel and the panel itself.

  - The Contractor shall be responsible for properly leveling the panels, and ensuring all access doors are operable.

  - The Contractor shall be responsible for connecting the control house ground to newly installed control panels.

  - The Contractor shall be responsible for providing & installing wire-way, race-way or conduit system a rigid pathway for the cable to make transition between existing substation cable tray and the new panels such that undue stress is not placed on the control cables such as RGS conduits.

  - The Contractor shall be responsible for modifying existing wire-ways and conduits to fit the new control panels.

  - All cables pulled to the control panels shall be sized to reach the floor of the panel and back to the top of control panel.

### GPS ANTENNA INSTALLATION

  - The Contractor shall be responsible for appropriately mounting the GPS Antenna to the exterior of the Control House roof or wall as appropriate.

  - The Contractor shall be responsible for creating an appropriate opening for wiring from the GPS Antenna to be run inside the Control House via conduit if an existing opening is not available.

  - The Contractor shall be responsible for providing conduits and fittings needed for GPS antenna installation.

### DC PANEL & DC BREAKERS INSTALLATION

  - The Contractor shall be responsible to purchase and install DC Panels and their breakers: DCP2-1, DCP2-2, DCP1-1, and DCP1-2 in this order. Refer to low voltage (LV1) drawings for detailed notes in instructions.

  - The Contractor shall be responsible for providing all required cable for DC panel installation, and DC cable going to the existing or new DC panels.

  - The Contractor shall be responsible for moving all load circuits from existing DC main panel to new DC panel as specified in the Low Voltage LV1 drawings.

  - The Contractor shall be responsible for removing existing DC main panel from service, removing cabling and removing panel from wall.

  - The Contractor shall be responsible for moving all load circuits from existing EM1 & EM2 panels to new DC panel as specified in the Low Voltage LV1 drawings.

  - The Contractor shall be responsible for removing existing DC panels from service, removing cabling and removing panel from wall. Existing cables can be reused if there are no signs of damage and sufficient length to reach the breaker. The Contractor shall demonstrate to the Project Representative that sufficient slack exists.

  - The Contractor shall be responsible for installing new DC panels in location shown in Low Voltage plan and details provided by JEA. Refer to NM172LV1 (DC) & NM172LV2 (DC) drawing for more details.

  - The Contractor shall be responsible for furnishing & installing Battery Cart Boxes (Qty. 2) as per NM172CH3.

### AC PANEL CABLES

  - The Contractor shall be responsible for procuring, running & terminating AC cable between control house AC panel and newly installed Relay Control Panels.

### CONDUIT INSTALLATION

  - The Contractor shall be responsible for installing aluminum conduit as specified in the conduit schedule, control house conduit plan (NM172CE1).

  - The Contractor shall be responsible for verification of all conduit lengths. Conduit lengths listed in the conduit schedule are approximate.

  - The Contractor shall be responsible for following construction notes a specified in drawings Control House Conduit Plan (NM172CE1).

  - The Contractor is responsible for all hardware necessary to complete the installation of the Conduit system.

  - The Contractor shall provide and installed labels on all newly installed conduits as part of this work.

### CABLE TRAY

  - The Contractor shall procure and install temporary cable tray system inside the control house as per (NMC596, and NMC597)

  - The Contractor shall be responsible for furnishing and installing miscellaneous items for the cable tray additions.

### INVESTMENT RECOVERY

SPCP will be coordinating internally with Investment Recovery Operations (IRO) in regards to the proper disposal of the scrap metal and control cable removed from service.  All salvageable material, i.e. demoed copper cable, panels, relays, are property of JEA.    When the Contractor commences work, there will be two scrap metal containers (one for the scrapped steel and one for the control cable) and it is the Contractor responsibility to perform the following:

  - The Contractor shall be responsible to properly dispose of the scrapped steel into the proper container that is located on site (JEA will have the containers properly labeled to prevent confusion).

  - The Contractor shall be responsible to properly dispose of the control cable into the proper container that is located on site (JEA will have the containers properly labeled to prevent confusion).

  - The Contractor shall NOT put any form of trash into the two scrap metal containers that are dedicated for scrap metal and control cable.

  - The Contractor shall be responsible for disposing of all trash that is a byproduct of their work regardless if the trash was created by material that was given by JEA such as empty cable reels.

### OUTAGE SUPPORT

  - The Contractor to provide personnel and equipment on-site during the outage for outage support.

  - Activities will include support JEA forces and running temporary control house cables.

### WEEKLY REPORTS

The Contractor’s field superintendent shall be responsible for filling out weekly reporting forms to coordinate with JEA’s Project Manager. The weekly reports shall be transmitted to JEA’s Project Manager via email on Friday EOB.