# NSCT Fire Protection Systems Upgrade

# Scope of Work

# FY25 & 26

Project #8010092

| Revision | Description | Date |
| --- | --- | --- |
| 0 | Bid Issue | 12/16/2024 |

- Table of Contents

1.0	General Work Scope	2

2.0	Codes and Standards	3

3.0	General Requirements	3

4.0	Reference Drawings and Reports	4

# General Work Scope

## JEA is seeking a licensed and experienced contractor to upgrade the CO2 Fire Protection Systems (FPSs) on 4 combustion turbine units at Northside Generating Station, units NSCT3, 4, 5 and 6, on a turnkey basis. The FPSs for these units are total flooding CO2 systems with a shared control panel, tank, header for each pair of units, and cover 4 compartments for each unit: generator/turning gear compartment, accessory/MCC compartment bearing tunnel, and the turbine/load compartment. Upgrades should bring units into compliance of NFPA Life Safety Requirements. This work includes:

### Replace the CO2 tanks with new 8-ton tanks for each pair of units.

### Replace the alarm panel on each unit to support new and current valves and components for each compartment.

### Install all electrical and controls cabling to allow DCS communication to the new panel.

### Replace the CO2 valves for each compartment to pneumatic time delayed valves.

### Add pneumatic sirens, bypass valves, and appropriate signage on all CO2 protected compartments.

### Install piping and fittings to incorporate the collector compartment on the low-pressure tank system for all units.

## Scope of Work

### Materials and Services to be Supplied by the Contractor

#### All necessary parts, including valves, fasteners, fittings, and piping shall be supplied by the Contractor.

#### All tools, temporary office facilities, scaffolding, lighting, and ventilation required by the Contractor to complete the work detailed in this scope.

#### Functionality testing at the conclusion of installation on each unit.

#### Labor and tools for preparation and staging of all components, including procurement of a crane, forklift, and/or flatbed truck, as necessary, as well as qualified operators for any such equipment.

#### All interface management with subcontractors.

#### Contractor to provide sanitary facilities.

#### Clean up and removal of all debris/waste and equipment associated with the Contractor's activity from jobsite.

### Materials and Services to be Supplied by JEA

#### JEA will ensure all relevant equipment is isolated safely and manage LOTO procedures and access.

#### JEA will provide limited 120V and 480V 3 phase power near the work location.  The Contractor must advise JEA of power requirements in advance, in order to schedule workload to supply power.

#### Contractor's employees shall be allowed use of parking facilities as specified by JEA.

# Codes and Standards

## Editions of codes and standards referenced below shall be those in effect on the date of the contract, except that if mandatory changes to applicable codes and standards become effective after the date of the contract, the mandatory code requirements will be incorporated.  It shall be the responsibility of the Contractor to inform JEA of the resulting effect.  Code cases shall not be used without the specific written approval of JEA.

## The Contractor shall identify any apparent conflict among standards, codes, and this specification to JEA upon discovery.  The Contractor shall obtain written resolution of such conflict from JEA prior to proceeding with Work involving the conflict.

## JEA is insured by Factory Mutual Insurance Company, also known as, FM Global. Attachment 4.1 lists the FM Global Property Loss Prevention Data Sheets. This reference provides the insurance company’s expected Fire Protection Inspection Frequency intervals.  The design proposal shall be emailed by the Contractor to JEA at burscm@jea.com and FM Global Plan Review at  engatlantaplanreview@fmglobal.com for JEA and FM Global to review and approve prior to construction.

## The following codes and standards are applicable to this specification:

### NFPA 12 Standard on Carbon Dioxide Extinguishing Systems

### NFPA 37 Standards for Combustion Engines and Gas Turbines

### NFPA 70 National Electrical Code

### NFPA 72 National Fire Alarm and Signaling Code

### NFPA 101 Life Safety Code

### NFPA 850 Recommended Practice for Fire Protection for Electric Generating Facilities

# General Requirements

## Contractor Safety Management Process

### Contractors shall adhere to JEA’s Contractor Safety Management Process which may be accessed online via the following link:

### https://www.jea.com/About/Procurement/Contractor_Safety/

## Schedule

### Where possible work requiring isolating or tagging out fire protection equipment will only be performed during scheduled outages.

### Tentative schedule for work during outages for the relevant units are as follows:

#### NSCT 3 and 4 – From May 5, 2025 – May 30, 2025 (26 days)

#### NSCT 5 and 6 – From April 5, 2026 – May 4, 2026 (30 days)

## Training and Permitting

### Some Contractor activities may require a JEA Hot Work permit. Contractor will obtain the Hot Work permit from JEA prior to the start of the activity requiring it.

### Contractor activities inside the affected compartments or other spaces may require confined space entry permits.  Contractor will be responsible for obtaining a confined space entry permit through JEA and all clearances required to commence work in the confined space.

## Contractor Personnel

### Contractor shall provide a listing of all key/skilled personnel to be assigned to the project.

### Contractor shall not remove key/skilled personnel without prior agreement from JEA.

### The Contractor’s superintendent shall remain on this installation through the completion of the project. The project shall not be “complete” until the satisfactory completion of the JEA clean-up inspection.

## Tools, Equipment, Temporary Workspace and/or Facilities, Lighting, and Ventilation

The Contractor shall coordinate their needs for laydown space, temporary workspace, or any field work facilities in writing with the JEA Project Manager for approval.

Details of the scaffolding, insulation, lighting, and ventilation equipment shall be coordinated with JEA Project Manager.

# Reference Drawings and Reports

## FM Property Loss Prevention Data Sheet 4-11N, Carbon Dioxide Extinguishing Systems

## Current System Drawings – Ansul

| JEA Control No. | Dwg No. | Description |
| --- | --- | --- |
| 400420 | 90759-M01 | Low Pressure CO2 Fire System Site Plan Generators 3&4 or 5&6 |
| 400421 | 90759-M02 | Low Pressure CO2 Fire System Generator Plan & Elevation Views |
| 400422 | 90759-M03 | Low Pressure CO2 Fire System Generator Section Views |
| 400423 | 90759-M04 | Low Pressure CO2 Fire System Detail Sheet |
| 400424 | 90759-M05 | Low Pressure CO2 Fire System Supply Piping Isometric |
| 400425 | 90759-M06 | Low Pressure CO2 Generator Piping Isometric |
| 400426 | 90759-M07 | Low Pressure CO2 Fire System Tank Connection Point Detail |
| 400427 | 90759-E01 | Low Pressure CO2 Fire System Detection and Control Equipment Locations |
| 400428 | 90759-E02 | Low Pressure CO2 Fire System Detection and Control Panel Layout |
| 400429 | 90759-E03 | Low Pressure CO2 Fire System Detection and Control Panel Layout |
| 400430 | 90759-E04 | Low Pressure CO2 Fire System Detection and Control Equipment Locations |
| 400431 | 90759-E05 | Low Pressure CO2 Fire System Detection and Control Panel Layout |