Headquarters - Procurement Department

225 North Pearl Street

Jacksonville, Florida 32202

October 29, 2025

ADDENDUM NUMBER: Two (2)

TITLE: Pole Line Hardware for JEA Inventory FY26 – FY31

JEA SOLICITATION NUMBER: 1412048646

BID DUE DATE: November 18, 2025

TIME OF RECEIPT: 12:00 PM

TIME OF OPENING: 02:00 PM

THIS ADDENDUM IS FOR THE PURPOSE OF MAKING THE FOLLOWING CHANGES OR CLARIFICATIONS:

- Changes:

ITEM ID: STAPL002

The following changes have been made to the list of approved manufacturers due to the staples not being barbed:

NOT APPROVED

CHANCE  9153

L&J INDUSTRIAL  1538162—C

APPROVED

ALLIED BOLT  22096

MACLEAN   J7656

- Changes:

ITEM ID: STAPL003

The following changes have been made to the list of approved manufacturers due to the staples not being barbed:

NOT APPROVED

CHANCE  9154

L&J INDUSTRIAL  2050162-C

APPROVED

ALLIED BOLT  22099

MACLEAN   J7672

- Changes: 1412048646 Addendum 2 Appendix B – Response Workbook is attached with the above changes highlighted on rows 660 and 661.

- Question: Do you have any information on why the Maclean DS-35M is not approved on this item?

Answer: The Maclean deadend insulator was removed from standards because the width of the thimble-eye on the insulator was too wide for the clevis on our approved fiber extension (INSFE001 & INSFE002). The width of the thimble-eye needs to be less than .83 inches.