TECHNICAL SPECIFICATION

FOR

NORTHSIDE GENERATING STATION

CONTINUOUS SHIP UNLOADER (CSU)

FY26

REPAIR UPPER AND LOWER GUIDE RAILS

FY27

REPLACE CSU BUCKETS AND CHAIN

PWO 31539758 (Engineering Support)

PWO TBD (Work Completion)

Revision: 00

Date7/9/2025

TABLE OF CONTENTS

Section	             Description

1.0		General

2.0		Work and Material to Be Furnished by Contractor

3.0		Work and Material to Be Furnished by JEA

4.0		Startup / Commissioning

5.0		Risks

6.0		Supporting Documentation

## General

  - Basis of Request

The chains and buckets on the Continuous Ship Unloader (CSU) are set to be replace on a Preventative Maintenance (PM) Work Order (WO) every 5 years. They were last replaced in 2021 and are currently scheduled to be replace in 2027, at the 6-year mark. Due to the necessity of the CSU to offload fuel and limestone vessels at Northside Generating Station (NGS), coupled with a 4-month lead time for replacement parts, it is imperative to ensure the components are replaced and remain in a working order to prevent costly ship delays.

Also, upon equipment overview, as seen in the pictures below, the chain guide rails have become heavily worn and need to be replaced as soon as possible to prevent CSU failure and causing additional equipment damage. Due to the long lead time and scheduled replacement of the chains and buckets, replacement of worn steel must be made before the installation of the new buckets and chains. This project is proposed to be split between FY26 and FY27 to accommodate the guide rail replacement steel and to maintain the maintenance schedule of the buckets/chains/sprocket.

  - Scope of Work

    - Although a shutdown is not required, coordination with operations and material handling is needed to complete the work while a fuel or limestone shipment is not scheduled or needed.

    - Alliance Contractor to order replacement steel and replace the worn sections of the upper and lower guide rails in FY26.

    - JEA to go out for bid for new upper sprocket, bucket, and chain components in FY26.

    - JEA to order new upper sprocket, bucket, and chain components in FY26.

    - Alliance Contractor to remove old upper sprocket, chain, and buckets and dispose of them in FY27.

    - Alliance Contractor to install new upper sprocket, chain, and buckets and verify alignment in FY27.

## Contractor Responsibilities

## FY26 Repairs:

## Contractor to Order new steel and hardware to replace the worn sections of the upper and lower guide rails for CSU at Northside Generating Station Dock.

## Replace the worn sections of upper and lower guide rails. Due to lack of accessibility to inner surfaces of guide rail complete extent of needed replacement is unknown and will be addressed during completion of this section of the project.

## Removed sections to be disposed of in JEA provided dumpsters.

## FY27 Chain and Bucket Replacement:

    - Provide all equipment, labor and materials to remove eight (8) segments of existing sprocket on each side, two(2) segments at a time, due to the chain interference and install the new sprocket sections. The sprocket will have to be rotated by JEA to provide access for the Contractor. Verify that the teeth on each sprocket section are level to the adjacent sprocket teeth. The existing sprockets are 5/8" out from one side to the other. Develop a plan to align the new sprockets. Mechanically clean both sides of each sprocket wheel and paint with two brush coats of ZRC. Provide new M20 grade 8 hex head bolts, nuts and washers. Torque bolts to 439 ft.-lbs.

## The Contractor shall connect the 8 sections of chain with the long pins and rollers supplied by JEA into two (2) chains of 425 links on the dock. See attached drawing for orientation and sequence. Contractor must install the roller on the connecting pin.

## Provide equipment, labor and materials to attach the bucket connecting hardware to the new chain and install the 85 buckets to the chain on the dock.

## Buckets should be fully assembled onto new chain with the full chain, roller, and bucket assembly laid out and secured prior to beginning of rolling new chain assembly onto CSU.

## Provide equipment, labor and materials to remove the pins from the existing chain at the toe of the foot and connect the new chain to the existing chain. See attached drawing.

## Remove all old chain and make final connection of the new chain.

## Site Cleanup

## Dispose of scrap in JEA provided dumpsters.

## Have JEA inventory the old buckets to determine those which will be removed and stored at a specified location on site by the Contractor. Removed buckets deemed salvageable by JEA shall be placed on the grassy area south of the intake flume. Remove buckets from the chain. Removal must not damage the bucket or its attachment lugs.

## Scrap the remaining chain and buckets.

## Remove all construction debris from site.

## JEA Responsibilities

## FY26 Repairs:

    - Provide a project manager/coordinator to assist in the timely removal and reinstallation of the Upper and Lower Guide Rails of CSU.

    - Coordinate the completion of the work during a period in which fuel or limestone will not be delivered via ship or barge.

    - Operate CSU to locate into require position to complete work and perform Lock Out/Tag Out of CSU to allow for safe completion of guide rail repairs.

    - Provide adequate facilities for the removal of scrap materials from jobsite.

  - FY27 Chain and Bucket Replacement:

    - Provide a project manager/coordinator to assist in the timely removal and reinstallation of the CSU buckets and chains.

    - Coordinate the completion of the work during a period in which fuel or limestone will not be delivered via ship or barge.

    - Separate from installation, chain/buckets/sprocket to be sent out for bid.

    - JEA will provide the new sprocket segments.

    - JEA will provide the chain (Chain Links are standard Caterpillar CAT 3P1113 Chain Links) with guide rollers and connecting bars assembled in 8 sections and new buckets.

    - JEA will provide knowledge on best practices and past experience to accomplish installation as well as an operator to control the CSU.

    - JEA will position the CSU in its repair location on the dock and orient the foot per drawing 1CSU6-02-0001.

    - JEA will move the CSU to pull the new buckets and chain up the tube while the old chain and buckets rests on the dock.

## Startup and Commissioning

  - Coordinate between JEA and Alliance Contractor to perform system testing and remediate any deficiencies.

  - The Contractor shall provide a final report with documented replacements of worn section and of new components.

## Risks

  - High-Cost

    - Due to instability in the market increased rates and tariffs could drastically increase the cost of the project.

  - Long Lead Time

    - Due to instability in the market, already long lead times could increase and lead to shifts in scheduling and work completion.

  - Shutdown Needs

    - Although a shutdown is not required, coordination with operations and material handling is needed to complete the work while a fuel or limestone shipment is not scheduled or needed.

  - Working on Energized Equipment

    - To install new chain the CSU must be operated with pins removed. This places the equipment in an abnormal condition and care must be taken during this process.

  - Working on Elevated Equipment

    - Sections of the work must be performed at high elevations and care must be taken to ensure fall protection for equipment and workers.

  - Live Load Capacity

    - Live load capacity of the CSU dock area is 250 lbs. per square foot.

## Supporting Documentation

## Site Location:  4377 Heckscher Dr, Jacksonville, FL 32226

- NGS FUEL & LIMESTONE UNLOADING DOCK

  - Equipment Images:

Existing System

- Drawing: 1CSU6-01-0001

- Drawing: 1CSU6-02-0001 (1/2)

- JEA Control Number: 309529

- JEA Control Number: 309530

- JEA Control Number: 309531

- JEA Control Number: 309532

- JEA Control Number: 309533