Procurement Department Bid Office

225 N. Pearl Street

Jacksonville, FL 32202

June 8, 2026

ADDENDUM NUMBER: Two

TITLE: Breaker Testing & Breaker Testing Report

JEA IFB NUMBER: 1412173248

PROPOSAL DUE DATE: June 11, 2026 June 17, 2026

TIME OF RECEIPT: 12:00 PM

THIS ADDENDUM IS FOR THE PURPOSE OF MAKING THE FOLLOWING CHANGES OR CLARIFICATIONS:

JEA is extending the bid due date to: June 17, 2026

JEA is providing the following Forms:

1412173248 Addendum 2 Appendix C - Breaker Testing Drawings

1412173248 Addendum 2 Appendix C - Previous Spend

JEA is responding to the following questions as shown below:

- Question:

Required Breaker Testing Method

Answer:

Secondary Injection Test is acceptable on the units that support this option, otherwise it has to be primary current injection test.

- Question:

Please provide all available one-line diagrams, panel/MCC/switchgear drawings, breaker manuals, trip unit curves/settings, and any available breaker data needed to prepare the testing plan and pricing.

Answer:

See attached 1412173248 Addendum 2 Appendix C - Breaker Testing Drawings

- Question:

Please clarify the process, duration, and format for the required JEA safety certification for contractor personnel. Is this an online or in-person training, and must it be completed once per contract or separately for each facility/site?

Answer:

JEA Safety qualification is not site specific.

Respondent shall be in compliance with JEA’s Contractor Safety Management Process policy.  JEA may reject the company's Response and proceed to Award to the next responsive and responsible Respondent if not in compliance.

JEA Safety information is available online at http://www.jea.com/About/Procurement/Contractor_Safety under Contractor Safety Management Process.  It is the Respondent’s responsibility to ensure it is following the JEA Safety policy. A list of the JEA's Safety Qualified vendors can be found on https://www.jea.com/About/Procurement/Contractor_Safety/. For additional information, contact Jim Fisher at (904) 229-5045 or Curtis Stothers at (904) 665-7736.

Each Company once awarded a JEA Contract is required to provide regular and continuing training for their employees.  Such training shall not be charged to JEA as a separate billable fee. Company (including General / Prime Contractors) will also monitor the training activities of Subcontractors under their direction.  All training outside of JEA specific training must meet OSHA requirements. Company employees working on JEA projects or sites shall receive JEA Safety Orientation and JEA Site-Specific Training before beginning work.

- Question:

Please also confirm JEA badging, background check, site safety training, escort, and security personnel requirements, including expected lead time and whether any direct cost will be reimbursable

Answer:

Work will be coordinated to work with O&M group, and an E&I will be at each facility to escort and give access to equipment.

- Question:

No-Escalation Language vs. CPI Adjustment Clause

Answer:

The annual CPI adjustment clause in Solicitation Section 2.20 applies after the first year, overriding the no   escalation language found in Appendix A.

- Question:

5Historical Spend / Prior Usage?

Answer:

See attached 1412173248 Addendum 2 Appendix C - Previous Spend.

- Question:

Is there a specific schedule or time frame to do the breaker testing?

Answer:

JEA is planning to do breaker testing during the months of June, July, August and September. The intention is to do the maximum facilities possible during those months. We are planning to do the facilities primarily on Tuesdays and Thursdays but may have the need to use other days of the week between Monday and Friday.

- Question:

Clarification for temporary power.

Answer:

JEA will bring temporary generators to power certain motor/pumps and controls panels during outage and testing in order to keep the facility in operation/production. The Contractor shall bring their own backup power or battery powered equipment for testing purposes.